## Risk Assessment
FGI 2010/ASHRAE 2008
| ACH | Pressure | Temp | RH | Risk H/M/L | ES Monitor Air Changes | ES Monitor Pressures | ES Monitor Temp/Hum. Yes/No | Monitoring Frequency | Monitored By | ASHRAE Temp Range | Notification Criteria | ASHRAE Humidity Range | Notification Criteria | Department Notification
Main Operating Suite Room Area
Operating Rooms | 20 | Pos | 68-75 | 30-60 | High | Continuous | Yes | Yes | Continuous | Eng- BAS or TT | 68-75 | ADOS | 30-60% | +/- 10% for 8 hrs/24 hr
Sterile Storage Rooms | 4 | Pos | 72-78 | Max 60 | Med | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | max 60% | +/- 10% for 8 hrs/24 hr
Sterile Core | 4 | Pos | 72-78 | Max 60 | High | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | max 60% | +/- 10% for 8 hrs/24 hr
Main Operating Suite Room East Area
Operating Rooms | 20 | Pos | 68-75 | 30-60 | High | Continuous | Yes | Yes | Continuous | Eng- BAS or TT | ADOS | ADOS | 30-60% | +/- 10% for 8 hrs/24 hr
Sterile Storage Rooms | 4 | Pos | 72-78 | Max 60 | High | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
Sterile Core | 4 | Pos | 72-78 | Max 60 | High | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
Ambulatory Surgery Center
Operating Rooms | 20 | Pos | 68-75 | 30-60 | High | Continuous | Yes | Yes | Continuous | Eng- BAS or TT | ADOS | ADOS | 30-60 | +/- 10% for 8 hrs/24 hr
Sterile Storage Rooms | 4 | Pos | 72-78 | Max 60 | Med | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
Sterile Core | 4 | Pos | 72-78 | Max 60 | Med | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
CSS Cleanroom | 4 | Pos | 72-78 | Max 60 | Med | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
CSS Decontam. | 6 | Neg | 72-78 | N/R | High | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | N/R | +/- 10% for 8 hrs/24 hr
Labor & Delivery
Operating Rooms | 20 | Pos | 68-75 | 30-60 | High | Continuous | Yes | Yes | Continuous | Eng- BAS or TT | ADOS | ADOS | 30-60 | +/- 10% for 8 hrs/24 hr
Adult and Pediatric Cath Labs
Cardiac Cath Procedure Rooms | 15 | Pos | 70-75 | 30-60 | High | Continuous | Yes | Yes | Continuous | Eng- BAS or TT | 70-75 | +/- 5 degrees 8hrs/24 hrs | 30-60 | +/- 10% for 8 hrs/24 hr
Digestive Disease Clinic
Endo Procedure Room | 15 | Pos | 68-73 | 30-60 | High | Continuous | Yes | Yes | Continuous | Eng- BAS or TT | 68-73 | +/- 5 degrees 8hrs/24 hrs | 30-60 | +/- 10% for 8 hrs/24 hr
Scope Processing
Scope Cleaning Room | 10 | Neg | N/R | N/R | High | Annually | Yes | Yes | N/A | Eng- BAS or TT | NR | +/- 5 degrees 8hrs/24 hrs | N/R | +/- 10% for 8 hrs/24 hr
CSS
Decontamination | 6 | Neg | 72-78 | N/R | Med | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | N/R | +/- 10% for 8 hrs/24 hr
Cleanroom | 4 | Pos | 72-78 | N/R | Med | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | N/R | +/- 10% for 8 hrs/24 hr
Supply Chain
Sterile Supply Storage | 4 | Pos | 72-78 | Max 60 | Med | Annually | Yes | Yes | Continuous | Eng- BAS or TT | 72-78 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
Bronchoscopy
Procedure & scope cleaning rooms | 12 | Neg | 68-73 | N/R | Med | Yes | Yes | Yes | Continuous | Eng- BAS or TT | 68-73 | +/- 5 degrees 8hrs/24 hrs | N/R | +/- 10% for 8 hrs/24 hr
Isolation Rooms
Infectious Airborne Rooms | 12 | Neg | 70-75 | Max 60 | High | No | Yes | Yes | Annual | Eng- BAS or TT | 70-75 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
Protective Environment | 12 | Pos | 70-75 | Max 60 | High | No | Yes | Yes | Annual | Eng- BAS or TT | 70-75 | +/- 5 degrees 8hrs/24 hrs | Max 60 | +/- 10% for 8 hrs/24 hr
ETC
Trauma Room | 15 | Pos | 70-75 | 30-60 | High | Annual | Yes | Yes | Annual | Eng- BAS or TT | 70-75 | +/- 5 degrees 8hrs/24 hrs | 30-60 | +/- 10% for 8 hrs/24 hr
ADOS- At Discretion Of the Surgeon
TT - TempTrak