ATTACHEMENT TITLE:		EMERGENCY GENERATOR TEST CRITERION

ATTACHMENT NUMBER:		ATT-16

## APPLICABLE POLICY:			C-105, C-106, C-107, C-108, C-109, C-110, C-111, C-112, C-113, C-114

| BUILDING / FLOOR / ROOM | EQ INFO / PM TAG | GENSET RATING ( KW ) | NAMEPLATE VOLTAGE | # NAMEPLATE AMPACITY | CALCULATED AMPACITY | CONNECTED LOAD ( AMPS ) | ### CRITERIA LOADS | TEST LOAD AMPS | MEETS CRITERION | TESTED USING |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | 30% NAMEPLATE |  |  |  |
| Boyd Tower LL BT0006 | Waukesha 12-232-001 | 965 | 277 / 480 3 Phase | 1451 | 1451 | 959 | 435 | 740 | Yes | Load Bank |
| General Hospital LL B10 | Detroit 12-232-002 | 965 | 277 / 480 3 Phase | 1451 | 1451 | 1117 | 435 | 515 | Yes | Load Bank |
| South Wing (South) LL2 S5A | #### Caterpillar 12-232-003 | 400 | 277 / 480 3 Phase | 600 | 600 | 445 | 180 | 280 | Yes | Load Bank |
| Carver (North) LL2 0086-4 | Caterpillar 12-232-005 | 1400 | 277 / 480 3 Phase | 2104 | 2104 | 1432 | 630 | 740 | Yes | Load Bank |
| Carver (South) LL2 0086-4 | Caterpillar #### 12-232-006 | 800 | 277 / 480 3 Phase | 1202 | 1202 | 134 | 361 | 435 | Yes | Load Bank |
| Colloton (East) LL2 0350E | #### Waukesha 12-232-007 | 1200 | 277 / 480 3 Phase | 1804 | 1804 | 942 | 541 | 805 | Yes | Load Bank |
| Colloton (West) LL2 0695A | Caterpillar 12-232-008 | 1252 | 277 / 480 3 Phase | 1917 | 1882 | 911 | 575 | 700 | Yes | Connected load |
| Pappajohn LL2 0740SB | Detroit 12-232-009 | 1200 | 277 / 480 3 Phase | 1804 | 1804 | 1852 | 541 | 915 | Yes | Load Bank |
| Pomerantz (Center) LL3 00002 | #### Caterpillar 12-232-011 | 900 | 277 / 480 3 Phase | 1354 | 1354 | 807 | 405 | 535 | Yes | Load Bank |
| Pomerantz (West) LL3 00002 | Caterpillar 12-232-010 | 1250 | 277 / 480 3 Phase | 1878 | 1878 | 1512 | 560 | 935 | Yes | Load Bank |
| Pomerantz (East) LL3 00002 | Kohler 12-232-012 | 1300 | 277 / 480 3 Phase | 1955 | 1955 | 537 | 587 | 950 | Yes | Load bank |
| Center for Disabilities and Deveopment LL CDDM2 | Cummins 12-232-013 | 230 | 120/208 3 Phase | 399 | 399 | 190 | 240 | 50 | No | Connected Load |