| SUBJECT/TITLE: | Pomerantz Diesel Emergency Generator #3 |
| --- | --- |
| PURPOSE: | To insure generators work . |

PROCEDURE:

POMERANTZ PAVILION DIESEL EMERGENCY GENERATOR #3 TESTING PROGRAM

THE POMERANTZ PAVILION EMERGENCY GENERATOR SET #3 IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

POMERANTZ PAVILION Emergency Generator #2 is a Kohler Generator set, operating at 277/480 Volts, and is located in room PFP 00002-SB

A. TEST RUN TIME 1 HOUR

1. Record fuel level in fuel tracking folder

2. Check the OIL Level and the Radiator Coolant Level of the engine, if either are low add  to bring

up to proper operating levels. The Coolant level can be checked from the radiator in PFP 00154-Y.

3. Turn selector switch in Generator #1 control cabinet to OFF. Open the MAIN breaker on Generator #1 in PFP 00002, close cross tie breaker  in GDP #1 Sec #16 in PFP 00002.  Close cross tie breaker in GDP#3 Sec #3 in PFP 00002.

4. Start the PFP #3 Diesel generator set, located in PFP 00002-SB,  by opening the normal breaker feeding TSA-Y(11-112-140) located in NDP #3 SECTION #5 BREAKER #1, thus causing a complete cold start. The emergency power should be available within 10 seconds.

5. CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR CONTROL CABINET FOR THE CORRECT VOLTAGE FOR THE GENERATOR OUTPUT.

6. Manually Transfer TS-M6 11-112-138 located in PFP 00005 to Emergency Power.

7. Manually Transfer TS-M2 11-112-134 power located in PFP 00005 to Emergency Power by putting toggle switch in manual mode and then toggling to Emergency Power.

8. Check any Air handlers or Pumps that should be running, have them restarted if 	necessary.

9. CHECK THE RADIATOR FANS, LOCATED PFP 00154-Y, THAT THEY ARE RUNNING

10.	Check and Test all Isolate/Bypass Transfer Switches for Proper Operation.

11.	Record the readings from the POWERLOGIC METER in the Generator’s control 	Cabinet into the Generator’s Log Book

B. AFTER THE TEST RUN IS COMPLETE

1. Transfer TS-M6 11-112-138 located in PFP 00005 to Normal Power.

2. Transfer TS-M2 11-112-134 located in PFP 00005 to Normal Power with toggle switch then return other toggle to Automatic

3. Close the normal breaker feeding TSA-Y(11-112-140) located in NDP #3 SECTION #5 BREAKER #1. There is a five minute cool down built into the Transfer Switch.

4. Check and Verify that all Transfer Switches are back in there Normal Power Positions and there are NO tripped breakers.

5. Return all cross tie breakers to open position. Close Generator #1 breaker. Place selector switch on Generator #1 control cabinet to AUTOMATIC POSITION.

6. Check any Air Handlers or Pumps that should be running are,  have them restarted if necessary.

7. Let the GENERATOR SET time out and shut down. Generator should shut down 5 minutes after transfer switch TSA-Y(11-112-140) returns to normal power.

8. Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS CLOSED.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115