| SUBJECT/TITLE: | Failure of Direct Expansion (D/X) Chiller |
| --- | --- |
| PURPOSE: | To maintain operation of DX Chiller. |

A. PROCEDURE:

1.	Check Building Automation System Monitoring screen or chiller control panel 		for chiller status, operation code and/or safety code that would indicate what 		kind of malfunction occurred.  If unit is not on a Building Automation System 		or does not have a digital control panel, check the following:

a. Ensure proper voltage is being supplied to unit.

b. Check safety control devices for tripped condition that would indicate 			type of malfunction and possible manual reset.  Never by-pass any 	safety 			control device.

c. Ensure the primary chilled water pump is on and proper water flow has 			been established through the flow switch.  If pump has failed, see 				Policy number C-320.   Never by-pass the flow switch.

d. Air Cooled Condenser

1. Ensure all condenser fans are operational.

2. Ensure condenser coil is clean.

e. Water Cooled Condenser (Deep well)

1. Ensure deep well pump is on and flowing water.  If 					     deep well has failed, see Policy number C321.

2. Ensure proper water flow through condenser.

f. Water Cooled Condenser (City Water)

1. Ensure proper water flow through condenser.

g. Water Cooled Condenser (Cooling Tower)

1.	Ensure condenser water pump can run.  (Check in hand 					position) and proper water flow can be established 						through the flow switch.  If pump has failed, see Policy 					number C320.  Never by-pass the flow switch.

2.	Ensure tower basin water level is correct.  If low, check 					make-up water and valve operation.  If make-up water is 					working, check for large leak or malfunctioning bleed-off 					control.

3.	Ensure condenser water temperature is approximately 85 					degrees.  If high or low, check the following:

a. Ensure cooling tower fan is operational and speed or cycling 				     control is working properly.

b. Ensure condenser water by-pass valve is operational and is being 			     controlled properly.

c. Ensure proper water flow through tower spray headers and nozzles.

d. Ensure tower basin heaters are operational in cold weather.

e. High outside air temperature and humidity will affect the 				     evaporative cooling efficiency of the tower.  The wet bulb 				     temperature of the outside air would be the limit of the 					     cooling effect of the tower.

B.	After trouble shooting the system and correcting any problems, the chiller 			may be restarted.

C.	If the chiller will not start or run properly, recheck the system for a problem 		you may have missed.  If you cannot find the problem, call in personnel more 		familiar with the operation of the chiller.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Revised: July 27, 2001

Date Reviewed: April 21, 2016