| SUBJECT/TITLE: | Failure of MRI Chilled Water Flow or Temperature |
| --- | --- |
| PURPOSE: | To maintain operation of MRI area chilled water. |

A. PROCEDURE:

1.	Notify staff in M.R.I. at 356-2236 about the failure and the areas that are 			affected.

2.	Check main chilled water pumps (pumps 18, 19 and 20) located across from 		Air Handling Unit # 11 in JCP West Basement.

3.	Open up Honeywell panel across from Air Handling Unit # 11 on South wall 		and turn switch to on position.  This will open up valves that switch from West 		Chiller Plant Water to JCP backup chilled water, located in JCP Southwest 		Basement.

4.	Main chilled water valves for room 0413-A are located in JCP West 			Basement above Security cage offices.  Main chilled water valves for room 		0432 are located between Air Handling Units # 4 and # 13 in JCP West 			Basement.

5.	Turn on backup chilled water pumps and start the backup chiller located in 		JCP Southwest Basement.  (Start chiller by opening chiller panel and 			switching toggle switch to on position.  Start up requires seven minutes.)

6.	Notify staff in M.R.I. at 356-2236 as to the status of the chilled water and the 		length of time required to effect repairs for their planning purposes.

7.	Reverse the above process when main chilled water is restored.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 22, 2016