| SUBJECT/TITLE: | Failure of Air Handling Unit #16 Main Chilled Water Flow or Temperature |
| --- | --- |
| PURPOSE: | To maintain operation of Air Handling Unit #16. |

A. PROCEDURE:

1.	Check main chilled water pumps, located in JCP West Basement.  (Pumps 		18, 19 and 20).

2.	If the JCP chilled water supply is down, open ball valves located by the back 		up pumps in JCP Southwest Basement, to feed Air Handling Unit # 16.  This 		is the backup cooling supply for the Air Handling Unit # 16.

3.	Close the two valves marked Main Chilled Water, located above clean steam 		boiler, in JCP Southwest Basement.

4.	Turn on the backup cooling pumps and start the backup chiller located in 			JCP Southwest Basement.  (Start chiller by opening chiller panel and 			switching toggle switch to on position.  Start up requires seven minutes.)

5.	Reverse the above process when main chilled water is restored.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 22, 2016