| SUBJECT/TITLE: | Failure of Main Chilled WaterAir Handling Unit #24 Administration Air Handling Unit Backup Cooling Change Over |
| --- | --- |
| PURPOSE: | To maintain operation of Air Handling Unit #24. |

A. PROCEDURE:

1.	Check main chilled water pumps (Pumps 1 and 2) located across from Air 			Handling Unit # 11 in JCP West Basement.

2.	If the JCP chilled water supply is down, open up two valves marked Backup 		Chilled Water, and close two valves marked Main Chilled Water, located 			above Air Handling Unit # 24.

3.	Turn on backup chilled water pumps and start the backup chiller located in 		JCP Southwest Basement.  (Start chiller by opening chiller panel and 			switching toggle switch to on position.  Start up requires seven minutes.)

4.	Reverse the above process when main chilled water is restored.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Servcies Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 22, 2016