	[image: image1.jpg]UNIVERSITY2/ TOWA
HOSPITALS s CLINICS

University of lowa Health Care





	
	Policy and Procedure Manual

	Engineering Services – JCP Main Chilled Water 
Air Handling Units #6 and #7                                                         C-327
                                         



	SUBJECT/TITLE:
	Failure of Main Chilled Water JCP Air Handling Units #6 and #7. Backup Cooling Change Over.

	
	

	PURPOSE:
	To maintain operation of Chiller Water Air Handling Units 6 and 7.  


A. PROCEDURE:


1.
Check Main Chilled water pumps (Pumps 1 and 2) located across from Air 

Handling Unit # 11 in JCP West Basement.


2.
If the JCP chilled water supply is down, open up Honeywell panel across from 

Air Handling Unit # 6 on east wall and turn switch to on position.  This will 

open up valves that switch from West Chiller Plant Water to JCP Backup 


Chilled Water, located in JCP Southwest Basement.  This will send backup 

chilled water to Air Handling Units # 6 and # 7.


3.
Turn on backup chilled water pump and start the backup chiller located in 


JCP Southwest Basement.  (Start chiller by opening chiller panel and 


switching toggle switch to the on position.  Startup will require seven 


minutes.)


4.
Reverse the above process when the main chilled water is restored.

Related and Supporting Documentation

•
Utilities Management Program, Engineering Services Policy C-001

•
Safety Reference Cards

•
On Call and Call Back Procedures, Engineering Services Policy A-115
Date effective: July 1, 1995
Date Reviewed: April 22, 2016 


C326 Administration Air Handler #24 
Page 1 of 1
C319 Failure of D/X Chiller
Page 2 of 1

[image: image1.jpg]