| SUBJECT/TITLE: | Failure of Chilled Water Bone Marrow Backup Cooling Change Over. |
| --- | --- |
| PURPOSE: | To maintain operation of Bone Marrow Unit Chilled Water. |

PROCEDURE:

1.	Check main chilled water pumps (Pumps 18, 19 and 20), located across from 		Air Handling Unit # 11 in JCP West Basement.

2.	If the JCP chilled water supply is down, switch chilled water flow from JCP 		West Basement pumps to JPP West Basement pumps.

3.	Close 4 large valves marked 7th Floor Equipment Room Chilled Water, 			located above the security cage in JCP West Basement (This will reroute 			water down from 7th.)  The valves are located in 7th Floor Equipment Room, 		by the chilled water header, located between the large condenser blower 			units.  There are four valves, to change to JPP chilled water, open two valves 		tagged “JCP MAIN CHILLED WATER,” and open valves tagged “JPP MAIN 		CHILLED WATER.”

4.	Reverse the above process when JCP Main Chilled water is restored.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 22, 2016