| SUBJECT/TITLE: | Failure of Main Chilled Water Air Handling Unit #14. |
| --- | --- |
| PURPOSE: | To maintain operation of Chilled Water Air Handler #14. |

A. PROCEDURE:

1.	Check main chilled water pumps located across from Air Handling Unit # 11 		in JCP West Basement.

2.	If the JCP chilled water is down, open up Honeywell panel across from Air 		Handling Unit # 14 on South wall, and turn switch to on position.  This will 		open up valves that switch from West Chiller Plant Water to JCP Backup 			Chilled Water, located in JCP Southwest Basement.  This will send backup 		chilled water to Air Handling Unit # 14.

3.	Turn on backup chilled water pumps and start the backup chiller located in 		JCP Southwest Basement.

4.	Reverse the above process when main chilled water is restored.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 22, 2016