| SUBJECT/TITLE: | Failure of Chilled Water Telecommunications Backup Cooling Change Over. |
| --- | --- |
| PURPOSE: | To maintain operation of Telecommunications Chilled Water. |

A. PROCEDURE:

1.	Check main chilled water pumps located across from Air Handling Unit # 11 		in JCP West Basement.

2.	Check Telecommunications booster pumps located by control air compressor 		JCP East Basement.

3.	Backup cooling chillers are located in Southeast corner of JCP East 			Basement.  The control panel is located on the South wall.

4.	Turn the switch on the panel to chiller position, and check other switch to 			see if it is on Chiller # 1.  (This is the air cooled unit.)  It takes approximately 5 		minutes for the chiller to start.  If it does not start after 5 minutes, check inside 		the chiller to see if chiller is in the start mode.  Try switching the switch to 		Chiller # 2. (This is the water cooled unit, be sure to open chilled water 			valve to this unit.)  Try turning on both booster pumps if neither chiller starts.

5.	Reverse the above process when main chilled water is restored.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 22, 2016