| SUBJECT/TITLE: | Failure of Pediatric Bone Marrow Air Handling Units #15 JCP |
| --- | --- |
| PURPOSE: | To properly manage air handler #15 shutdown. |

A. PROCEDURE:

1. WARNING:  Notify Pediatric Bone Marrow Transplant units prior to scheduled shut down, as soon as possible after unscheduled shutdown, and prior to start-up.
2. Failure to notify puts patients at risk.

B.	Notification

1. If either unit is found out of service for unplanned reasons, the charge nurse on each unit must be notified immediately.  For a planned shutdown (scheduled maintenance or repairs), the charge nurse on each unit must be notified before turning the air-handling unit off.  Proper notification requires you to complete a Bone Marrow Transplant Unit Air Handling Unit Interruption Notice.  The blank forms can be found in the RCP 8th Floor equipment room (RCP 8051), in the 3rd Floor JCP equipment room (JCP 3373), or in the Environmental Systems Shop.

C.	Completing Interruption Notice Form

1. A separate notice is required for each nursing unit.

2. Indicate which air-handling unit is or will be out of service by 					marking the form next to the area(s) served.

3. Indicate the Air Handling Unit is out of service (unplanned) or 				will be out of service.  For scheduled service fill in date and 					time of shutdown.

4. Indicate when the Air Handling Unit will be back in service by 				filling in the date and approximate time the work will be 					completed.

5. Indicate reason for outage.  (Off on low limit trip, scheduled 					maintenance, etc.).

6. Fill in contact name and phone number in case nursing unit 				    staff have any questions.

D.	Interruption Notification

1. Indicate if Adult or Child unit is being notified.

2. Have Charge Nurse sign on line AA and fill in date and time.

3. Remove pink copy and give to the Charge Nurse.

4. Shut off Air Handling Unit and complete required maintenance or repairs.

E.	Unit Back in Service Notification (prior to start-up)

1. Have Charge Nurse sign on line BB and fill in date and time.

2. Ask Charge Nurse how much time will be required to mask the 				patients before starting the Air Handling Unit(s).

3. Remove yellow copy and give to the Charge Nurse.

4. Wait the required length of time before starting the Air Handling 				Unit(s).

5. Return original copy to the Engineering Services Shop.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Operations Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: November 2, 2004

Date Reviewed: April 26, 2016