| SUBJECT/TITLE: | Access to Ceiling Space 3JCP Pediatric Bone Marrow Transplant |
| --- | --- |
| PURPOSE: | To properly access Pediatric Bone Marrow Ceiling Space |

A. PROCEDURE:

1. WARNING:  Failure to follow these instructions can release aspergillus into hallways and patient rooms.

2. This fungus is lethal to the Bone Marrow Transplant patient population.

3. If you have any questions or concerns, contact the Charge Nurse on duty in either Adult or Pediatric Bone Marrow Transplant.

a. Unless an extreme emergency, the ceiling in the hallway should be 			    entered on the evening shift, when the fewest number of patients are 			    in the hallway.  If work must be done in the ceiling of a patient room, or 		    a room patients use (classroom or playroom), the patient(s) must leave 			    the room and all supplies and belongings must be taken out of the 			    room.

b. Plastic barriers must be put up at all times prior to entering the ceiling.  The 	  	    barrier will be plastic sheeting from ceiling to floor completely enclosing the 	    	    access area, held in place with duct tape.  Contact the Structural Craft Shop 	 	    (353-6423) between the hours of 7:00 A.M. and 3:30 P.M., Monday through 	 	    Friday, for barrier installation.  On nights or weekends, the responding 	 	   	    mechanic must install the barrier, assisted by other Facility Operations or 	 	    Housekeeping staff.

c. Special gowns, shoe, and head covers should be worn before entering 			    the barrier and while working in the ceiling.  Any tool carts or 				    equipment should be left at the exit of the barrier, if possible.

d. Upon leaving the barrier, remove head cover and gown, and then remove one 	 	    shoe cover at a time, keeping the dirty foot (the one with the shoe cover) in the 	 	    barrier and placing the clean foot (the one without the shoe cover) outside the 	 	    barrier.  Leave all used shoe covers, head	covers and gowns near the exit of the 	    barrier for Housekeeping to remove.  If carts or equipment must go inside the 		    barrier, they must be covered with a sheet just prior to being removed from the barrier, and must then be taken immediately off the unit.  Absolutely no dust should be carried out of the barrier area.

e. At the completion of the work, Housekeeping should be notified to take down the barrier (assisted by Structural Craft), and perform clean up duties.  Housekeeping will need some prior notification, therefore, approximately 30 minutes before the completion of your project, ask the nursing unit clerk to call Housekeeping.  The housekeeper will put on gowns, shoe covers and head covers before entering the barrier.  They will vacuum the floor inside the barrier, put all disposable shoe covers and head covers in trash bags and place gowns near the barrier exit.  They will then remove their own 	head cover and gown, putting the head cover in a trash bag and the gown near the exit of the barrier.  They will also remove shoe covers as previously described, prior to coming out of the barrier.  The trash 	bag will be disposed of in the dirty utility room.  A clean sheet will be 	placed outside the barrier and all gowns placed on it.  The sheet will wrap all gowns and be placed in the linen bins.

f. Engineering Services will assist with removing the barrier and taking it 		              off the unit immediately. Housekeepers will vacuum the area again immediately.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 26, 2016