Policy Statement B-218

Attachment 1

PNEUMATIC TUBE SPILL RESPONSE

PROCEDURE:

When a suspected contamination has occurred (Level III) within the system, the following steps MUST be taken:

- Turn off the system at the Master Computer.  By clicking

- on the SPILL command, all blowers are stopped and all zones will cease transaction.

- Notify Security, as well as the Service Center (Phone Number 159) that a spill is suspected and that the system is unavailable until further notice.  Carriers are left where they are until the risk of contamination is evaluated by Maintenance/Engineering Staff. Notification is given to a select group. (Stations 152 and 131).

- Determine route of affected carrier(s) and note on mechanical riser.

- The entire pneumatic tube system (stations, transfer units, and shifters) shall be cleaned in accordance with Hospital Procedure (listed on following page under Decontamination Procedures/Level III).  It is important to note that first and foremost, the system MUST BE SHUTDOWN upon notification of a spill at any location within the Hospital.  Special attention will be given to known contaminated areas and devices.

- After proper cleaning of the tube runs and devices, the system may then be put in the PURGE mode by the Master Computer.  A determination will be made regarding the contamination status.  The carrier will then be sent to its intended destination, if it is found clean.

- After Maintenance/Engineering has determined that the affected tube runs and devices are clean, a complete purge has done and all carriers are out of the system, then the tube system will be brought back on line.  Staff from Maintenance/Engineering will then complete the Lab Incident Report to verify the spill level, time of interruption and when the system was brought back into service.