| SUBJECT/TITLE: | Medical Gas Compressed Gas Systems |
| --- | --- |
| PURPOSE: | To ensure a reliable med gas distribution system. |

Because of the potentially critical consequences of any problem associated with the therapeutic oxygen, medical compressed airs and vacuum distribution systems, the following guidelines shall be followed by Engineering Services.

1. PROCEDURE:

A.	Engineering Services shall cooperate with Respiratory Care in all ways 			necessary to ensure a reliable distribution system.

B.	Engineering Services shall notify or respond to Respiratory Care in a 			timely manner on any matter affecting distribution.

C.	Shutdown of any portion of the distribution system shall not be undertaken 		without notification of all Users on that portion of the system, the 				Operations Manager of Engineering Services and the Director of 				Respiratory Care.  In an emergency, notification shall be given as soon as 			possible after the emergency is under control.

D.	Respiratory Care shall maintain records on-site for the previous year of 			tests performed by Respiratory Care on patient interface outlets 				(reference UIHC Safety Program and Manual, section II.E.24).  				Records shall be maintained for an additional six (6) years in off-site 			storage.

E.	Permanent drawings shall be maintained in Engineering Services, 				showing the schematic layouts of the distribution system.  The layouts 			shall show the approximate location of all valving, valve tag numbers 			and clearly indicate areas affected by closing each valve.  Critical care 			areas shall be highlighted.  These drawings are to be reviewed and 				up-dated as needed, but not less than once each year (forth 					quarter of the calendar year) by Engineering Services

F.	The following valves shall be chained in the open position with “break 			away” chains that will serve as tamper indicators:

1.)	The main supply valves located on the piping just before it 					leaves the medical gas pad.

2.)	The main supply valves located on the piping as it enters the 				hospital complex.

3.)	A sign or signs shall be installed in the vicinity of each of the 				valve stating “CONTACT ENGINEERING SERVICES BEFORE 				CLOSING OXYGEN SUPPLY VALVES (356-2711).”

G.	The valves indicated in “F," the main building branch valves and each 			floor valve shall have the following wording on a permanent tag 				attached to the valve:  “OXYGEN, DO NOT CLOSE, CONTACT 				ENGINEERING SERVICES 356-	2711."

H.	 Once each year (first quarter of calendar year) a visual inspection shall 			also be made of the main building branch valves.  Problems observed shall 		be reported to the Service Center for processing.

I.	Engineering Services shall perform maintenance as needed to 				maintain the distribution system Records shall be kept in the Work 				Control Center.

J.	All portions of the distribution system that are affected by re-work 				shall be tested and prepared for patient service in accord with National 			Fire Codes, section 56G.  No system shall be placed back in service 			without the consent of Respiratory Care.

K.	Zone Valves will be closed only after coordination between 					Engineering Services and the Nursing staff.

Related and Supporting Documentation

•	Safety Reference Cards

•	UIHC Safety Manual

•	Preventive Maintenance, Engineering Services Policy C-003

•	Medical Air System/Vacuum Emergency Procedures, Engineering Services Policy C-201

•	Oxygen System Emergency Procedures Engineering Services Operations Policy C-207

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: June 20, 2001

Date Reviewed: July 25, 2016