| SUBJECT/TITLE: | Emergency Electrical System Failures During Normal Hours |
| --- | --- |
| PURPOSE: | To Restore Power |

A. The Emergency Electrical System within the University Hospital Complex is powered by various diesel generator sets, when there is a failure of incoming normal utility power there are automatic transfer switches in the Emergency Electrical System.  These are used to switch the riser lines to normal utility power or to the emergency generator.  The switches and generators are monitored in the Electrical Craft Shop, located in BT 0027.

Listed below are some recommended steps to follow if there is a failure of a generator or switch.

1.	GO TO THE ELECTRICAL SYSTEMS METER ROOM IN BT 0027

a. Go to the Electrical Craft Shop (Room BT 0027) and check the meter 		and alarm monitoring system to see what areas are out of power.

b. Check to see if the Emergency Power Generator is running, and that the 	transfer switches are in their proper positions.

c. Note anything that shows as an abnormal type of 	condition.

2.	LINES OF COMMUNICATIONS

a. If the Electrical Systems Supervisor is not present, page him or call him and 	inform him of the loss of Emergency Power.  If he cannot be reached, contact the 	Assistant Director, Chuck Weno at 356-1918.

b. Also notify the Service Center at 159 and Safety and Security at 356-2658 or 	by radio.

c. Check with the phone operator as to what calls they have received 	regarding loss of Emergency Power.

d. Explain to all personnel notified what in indicated on the monitor system 	regarding what is functional and what is not.

3.	NECESSARY TOOLS

a. Take appropriate tools

b. Carry a two way radio along also.

4.	OUTAGE AREA

a. Notify the area involved with the loss of Emergency Power that there is 		a problem with the Emergency Systems and that you are working to resolve it and 	will keep them informed of the situation.

b. Re-contact the area involved as soon as you can determine what the problem 	is and how long it will take to resolve the problem with the loss of Emergency 	Power.

5.	GENERATOR SET FAILURE

a. If the Emergency Generator set for the area without Emergency Power 		has stopped because of a failure shutdown alarm, check the alarm 	condition reset 	and restart the generator if possible.

b. If the generator set cannot be restarted, use the Emergency Cross Connection 	System for the generator set that has shut down. 	The instructions for using this 	system are located by each generator set’s control panel.

c. There is also a copy of these instructions in the Electrical Craft Shop, room 	BT 0027.

6.	TRANSFER SWITCH FAILURE

a. If the Emergency Generator set is running and producing power, check 		all the transfer switches in that particular system to see if they are in their proper 	positions.

b. If the transfer switch has not transferred some switches can be manually 	transferred if you open both sources, if not you will have to provide temporary 	power to the affected load from another source	.

c. Use caution when dealing with live electrical units.

7.	EMERGENCY ELECTRICAL SYSTEM RESTORED

a. After you have restored the Emergency Electrical System, and it is 			functioning properly, re-contact all you Lines of Communication, and also the 	personnel in the Outage area, to inform them that the system is functional.

8.	OUTAGE DATA COMPLETION

a. When the power outage is completely over, and all Normal Power is 		restored and the Emergency Power Generators are shut down, fill out all generator 	log books, and utility outage forms.  These forms are in the Electrical Craft Shop, 	room BT0027.  You will need to notify all personnel involved with the failure that 	Normal Power Utility is back on line.

9.	DIESEL TANK REFUELING

a. Diesel fuel stored in underground storage tanks will be enough to run 	generators for 3 to 8 days, depending on load and tank size.  If the power outage 	is expected to last for a day or more, contact the fuel vendor and make 	arrangements 	to refill tanks as needed.

B. Remember, these procedures may not be able to be followed in this exact order in all outage situations.  Every power outage is a little different.  It depends greatly on the area that is out, the people working in that area; the severity of the outage and the length of time the power will be out.  The main thing is to stay calm and do your job to the best of your ability.

C. Related and Supporting Documentation

1. Utilities Management Program, Facility Operations Policy C-001

2. Safety Reference Cards

3. On Call and Call Back Procedures, Facility Operations Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July1, 1995

Date Revised: July 6, 2007

Date Reviewed: April 12, 2016