| SUBJECT/TITLE: | General Hospital Diesel Emergency Generator Testing Program |
| --- | --- |
| PURPOSE: | To test General Hospital Generator |

GENERAL HOSPITAL DIESEL EMERGENCY GENERATOR TESTING PROGRAM

THE GENERAL HOSPITAL EMERGENCY GENERATOR SET IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

GENERAL HOSPITAL Emergency Generator is a DETROIT DIESEL Generator set, operating at 277/480 Volts, and is located in room GH-B9-G

TEST RUN TIME: 1 HOUR

LOAD TIME: 40 MINUTES

- Check the OIL Level and the Radiator Coolant Level of the engine, if either are low add  to bring

up to proper operating levels. The Coolant level can be checked from the radiator on the roof of Room GH-B-10.

- Use the load bank to load generator. A 400 KW load is required. Check settings on load bank.

Make sure the motor power selector switch is set to “INT 480”. The voltage toggle switch should

be set to 480.

- Use cross tie to connect load bank to generator. The load bank is connected to GDP #5 Breaker              #2 located in RCP 0086-SB.

- USE FOLLOWING INSTRUCTIONS TO IMPLEMENT CROSS TIE.

1.   OPEN CARVER GENERATOR #1 MAIN BREAKER

2.   CLOSE CROSS TIE BREAKER LOCATED IN SWITCH GEAR 11-110-			      031 IN RCP 0086-SB

3.   OPEN MAIN BREAKER ON ETC GENERATOR. BREAKER IS LOCATED 			      UNDER ETC GEN SET CONTROL PANEL.

4.   OPEN GDP#5 MAIN BREAKER LOCATED IN GENERATOR SWITCH 			      GEAR 11-110-033 LABELED “FED FROM ETC GENERATOR” REMOVE 			      KIRK KEY.

5.   INSERT KIRK KEY INTO LOCK ON BREAKER LABELED “FED FROM 			      RCP CROSS CONNECT” IN GENERATOR SWITCH GEAR 11-110-033

6.  CLOSE BREAKER “FED FROM RCP CROSS CONEECT”

7.  CLOSE CROSS CONNECT BREAKER LOCATED IN SWITCH GEAR 11-			      110-010 IN GH B-9-G. LOAD BANK IS NOW CONNECTED TO GENERAL 		 	     HOSPITAL GENERATOR

- Start the Diesel generator set, located in GH B 10, using the test switch on an ATS and by opening a normal breaker that feeds an automatic transfer switch, thus initiating a complete cold start. The emergency power should be available within10 seconds...

- CHECK THE RADIATOR FANS, LOCATED ON THE ROOF OF GH B 10, THAT THEY ARE RUNNING

- CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR

CONTROL CABINET FOR THE CORRECT VOLTAGE (480) FOR THE GENERATOR OUTPUT.

- At the load bank, turn “POWER ON”. Check load bank rotation by turning blower on. Air should move upward from load bank. If rotation is backward turn off blower and wait for blower to stop. Switch rotation using toggle and restart blower.

- Once rotation is correct turn “MASTER LOAD” toggle to “ON”.

- Add load to generator by using toggles switches. Add 50 KW at a time until you have a load of 400 KW.

- TRANSFER SWITCHES SHOULD HAVE NORMAL POWER AVAILABLE AND EMERGENCY POWER AVAILABLE INDICATOR BULBS ILLUMINATED. If  not, install new bulbs or make note if none available

- Check and Test all Auto/Bypass Transfer Switches for Proper Operation.

- Check any Air handlers or Pumps that should be running, have them restarted if necessary.

- Record the readings from the POWERLOGIC METER in the Generator’s control Cabinet into the Generator’s Log Book

AFTER THE TEST RUN IS COMPLETE

16. Unload generator by toggling the KW load to off. One toggle at a time. When all toggles are        off you can turn off “Master Load” Leave blower running until air above load bank cools to a 	         comfortable temperature. Usually ONE minute is enough.

- Check and Verify that all Transfer Switches are back in Normal Power Positions and there are NO tripped breakers.

- Check any Air Handlers or Pumps that should be running are, have them restarted if necessary.

- Let the GENERATOR SET time out and shut down. Generator should shut down 5 minutes after normal breaker used in step #3 for load is closed and transfer switch returns to normal power.

20.  USE FOLLOWING STEPS TO UNDO CROSS TIE.

a. OPEN CROSS CONNECT BREAKER LOCATED IN SWITCH GEAR 11-110-	  010 IN GH B-9-G.

b. IN RCP 0086-SB OPEN BREAKER “FED FROM RCP CROSS CONNECT”.   	    REMOVE KIRK KEY

c. INSERT KIRK KEY INTO LOCK ON BREAKER MARKED “FED FROM ETC 	       	    GENERATOR” IN SWITCH GEAR 11-110-033

d. CLOSE GDP#5 MAIN BREAKER IN SWITCH GEAR 11-110-033 MARKED 		     FED FROM ETC GENERATOR

e. CLOSE MAIN BREAKER ON ETC GENERATOR. BREAKER IS LOCATED 	  	    UNDER   ETC GEN SET CONTROL PANEL

f.  OPEN CROSS TIE BREAKER LOCATED IN SWITCH GEAR 11-110-031

g. CLOSE CARVER GENERATOR #1 MAIN BREAKER

- Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS CLOSED.

Related and Supporting Documentation

- Utilities Management Program, Facility Operations Policy C-001

- Safety Reference Cards

On Call and Call Back Procedures

Source: UI Healthcare Engineering Services

Date effective: July1, 1995

Date Revised: July 1, 2013

Date Reviewed: April 13, 2016