| SUBJECT/TITLE: | South Wing Diesel Emergency Generator Testing Program |
| --- | --- |

THE SOUTH WING EMERGENCY GENERATOR SET IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

SOUTH WING Emergency Generator is a Caterpillar Generator set, operating at 277/480 Volts. It is located in South Wing room S5

TEST RUN TIME: 1 HOUR

A. LOAD TIME: 40 MINUTES

1. Check the OIL Level and the Radiator Coolant Level of the engine, if either are low add  to bring them to proper operating levels. The Coolant level can be checked from the radiator on the roof South Wing by door S 825-S

2. Use the load bank to load generator. A 200 KW load is required. Check settings on the load bank.  Make sure the motor power selector switch is set to “INT 480”. The voltage toggle switch should be set to 480.

3. Use cross tie to connect load bank to generator. The load bank is connected to GDP #5 Breaker #2 located in RCP 0086-SB.

4.  USE FOLLOWING INSTRUCTIONS TO IMPLEMENT CROSS TIE.

a. OPEN CARVER GENERATOR #1 MAIN BREAKER

b. CLOSE CROSS TIE BREAKER LOCATED IN SWITCH GEAR 11-110-			031 IN RCP 0086-SB

c. OPEN MAIN BREAKER ON ETC GENERATOR. BREAKER IS LOCATED 			UNDER ETC GEN SET CONTROL PANEL.

e. OPEN GDP#5 MAIN BREAKER LOCATED IN GENERATOR SWITCH 			GEAR 11-110-033 LABELED “FED FROM ETC GENERATOR” REMOVE 			KIRK KEY.

f. INSERT KIRK KEY INTO LOCK ON BREAKER LABELED “FED FROM 			RCP CROSS CONNECT”IN GENERATOR SWITCH GEAR 11-110-033

g. CLOSE BREAKER “FED FROM RCP CROSS CONNECT”

h. CLOSE CROSS CONNECT BREAKER LOCATED IN SWITCH GEAR 11-			110-021 IN SW S5. LOAD BANK IS NOW CONNECTED TO SOUTH WING 			GENERATOR

5. Start the Diesel Generator set, located in room S5, by testing one of the AUTO/BYPASS switches connected to the generator. The emergency power should be available within10 seconds. Once the generator is running put generator control knob in manual run position.

6. CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR CONTROL CABINET FOR THE CORRECT VOLTAGE (480) FOR THE GENERATOR OUTPUT.

7. CHECK THE RADIATOR FANS, LOCATED ON THE ROOF OF SOUTH WING BY DOOR SW   S825-S, VERIFY THEY ARE RUNNING

8. At the load bank, turn “POWER ON”. Check load bank rotation by turning blower on. Air should move upward from load bank. If rotation is backward turn off blower and wait for blower to stop. Switch rotation using toggle and restart blower.

9. Once rotation is correct turn “MASTER LOAD” toggle to “ON”.

10. Add load to generator by using toggles switches. Add 50 KW at a time until you have a load of 200 KW.

11. TRANSFER SWITCHES SHOULD HAVE NORMAL POWER AVAILABLE AND EMERGENCY POWER AVAILABLE INDICATOR BULBS ILLUMINATED. If  not, install new bulbs or make note if none available

12. Check and Test all Auto/Bypass Transfer Switches for Proper Operation. Including ATS #17(11-112-148) located in GH-C-100

13. Record the readings from the POWERLOGIC METER in the Generator’s control Cabinet into the Generator’s Log Book

B. AFTER THE TEST RUN IS COMPLETE

1. Unload generator by toggling the KW load to off. One toggle at a time. When all toggles are off

you can turn off “Master Load” Leave blower running until air above load bank cools to a

comfortable temperature. Usually ONE minute is enough.

2. Check and Verify that all Transfer Switches are back in Normal Power Positions and there are

NO tripped breakers

3.  Turn the generator control knob back to auto.

4. Let the GENERATOR SET time out and shut down It has a 5 minute cool down period.

5. USE FOLLOWING STEPS TO UNDO CROSS TIE.

a. OPEN CROSS CONNECT BREAKER LOCATED IN SWITCH GEAR 11-110-	  	021 IN SOUTH WING ROOM S5

b. IN RCP 0086-SB OPEN BREAKER “FED FROM RCP CROSS CONNECT”. 	    	REMOVE KIRK KEY

c. INSERT KIRK KEY INTO LOCK ON BREAKER MARKED “FED FROM ETC 	GENERATOR” IN SWITCH GEAR 11-110-033

d. CLOSE GDP#5 MAIN BREAKER IN SWITCH GEAR 11-110-033 MARKED 	    	FED FROM ETC GENERATOR

6. CLOSE MAIN BREAKER ON ETC GENERATOR. BREAKER IS LOCATED 	  	    UNDER   ETC GEN SET CONTROL PANEL

7. OPEN CROSS TIE BREAKER LOCATED IN SWITCH GEAR 11-110-031

8. CLOSE CARVER GENERATOR #1 MAIN BREAKER

9. Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS CLOSED.

Related and Supporting Documentation

- Utilities Management Program, Engineering Services Policy C-001

- Safety Reference Cards

- On Call and Call Back Procedures, Facility Operations Policy A-115

Source: UI Healthcare Engineering Services

Date Effective: July 1, 1995

Date Revised: July 1, 2016

Date Reviewed: July 7, 2016