| SUBJECT/TITLE: | East Colloton Pavilion Diesel Emergency Generator Testing Program |
| --- | --- |
| PURPOSE: | To ensure emergency power to East Colloton Pavilion. |

EAST COLLOTON DIESEL EMERGENCY GENERATOR TESTING PROGRAM

THE EAST COLLOTON EMERGENCY GENERATOR SET IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

EAST COLLOTON Emergency Generator is a Waukesha Generator set, operating at 277/480 Volts, and is located in room JCP 0350E-SB

TEST RUN TIME 1 HOUR

A. LOAD TIME 40 MINUTES

1. Check the OIL Level and the Radiator Coolant Level of the engine, if either is low, add to bring up to proper operating levels. The Coolant level can be checked in the underground vault in room JCP 0350E-1.  Surge tank is accessed by climbing ladder.

2. Use the load bank to load generator. A 600 KW load is required. Check settings on load 	      	bank. Make sure the motor power selector switch is set to “INT 480”. The voltage toggle 	  	      	switch should be set to 480.

3. Use cross tie to connect load bank to generator. The load bank is connected to GDP #5	     Breaker #2 located in RCP 0086-SB.

4. USE FOLLOWING INSTRUCTIONS TO IMPLEMENT CROSS TIE.

a. OPEN CARVER GENERATOR #1 MAIN BREAKER

b. CLOSE CROSS TIE BREAKER LOCATED IN SWITCH GEAR 11-110-			031 IN RCP 0086-SB

c. OPEN MAIN BREAKER ON ETC GENERATOR. BREAKER IS LOCATED 			UNDER ETC GEN SET CONTROL PANEL.

d. OPEN GDP#5 MAIN BREAKER LOCATED IN GENERATOR SWITCH 			GEAR 11-110-033 LABELED “FED FROM ETC GENERATOR” REMOVE

KIRK KEY.

e. INSERT KIRK KEY INTO LOCK ON BREAKER LABELED “FED FROM 		     	RCP CROSS CONNECT” IN GENERATOR SWITCH GEAR 11-110-033

f. CLOSE BREAKER “FED FROM RCP CROSS CONNECT”

g. CLOSE CROSS CONNECT BREAKER LOCATED IN SWITCH GEAR			11-110-041 IN JCP 0350E-SB. LOAD BANK IS NOW CONNECTED TO  			JOHN COLLOTON EAST GENERATOR

5. Start the Diesel Generator set, located in room JCP 0350-E, by testing one of the

AUTO/BYPASS switches connected to the generator. The emergency power should be

available within10 seconds. Once the generator is running put generator control knob in

manual run position

6. CHECK THE RADIATOR FANS, LOCATED IN THE UNDERGROUND VAULT LOCATED IN JCP 0350E-1, VERIFY THEY ARE RUNNING

7. CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR

CONTROL CABINET FOR THE CORRECT VOLTAGE (480) FOR THE GENERATOR OUTPUT.

8. At the load bank, turn “POWER ON”. Check load bank rotation by turning blower on.

Air should move upward from load bank. If rotation is backward turn off blower and

wait for it to stop. Switch rotation using toggle and restart blower.

9. Once rotation is correct turn “MASTER LOAD” toggle to “ON”.

10. Add load to generator by using toggles switches. Add 50 KW at a time until you

have a load of 600 KW.

11. TRANSFER SWITCHES SHOULD HAVE NORMAL POWER AVAILABLE AND

EMERGENCY POWER AVAILABLE INDICATOR BULBS ILLUMINATED. If not, install new

bulbs or make note If none available

- Check and Test all Auto/Bypass Transfer Switches for Proper Operation.

- Record the readings from the POWERLOGIC METER in the Generator’s control Cabinet into the Generator’s Log Book

B. AFTER THE TEST RUN IS COMPLETE

1. Unload generator by toggling the KW load to off. One toggle at a time. When all toggles are off you can turn off “Master Load” Leave blower running until air above load bank cools to a comfortable temperature. Usually ONE minute is enough.

2. Check and Verify that all Transfer Switches are back in Normal Power Positions and there are NO tripped breakers.

3. PUT GENERATOR SELECTOR SWITCH TO AUTOMATIC

4. Let the GENERATOR SET time out and shut down. Generator has 30 second cool down time.

5. USE FOLLOWING STEPS TO UNDO CROSS TIE.

a. OPEN CROSS CONNECT BREAKER LOCATED IN SWITCH GEAR 11-110-041 IN JCP 0350-E SB

b. IN RCP 0086-SB OPEN BREAKER “FED FROM RCP CROSS CONNECT”.  	 REMOVE KIRK KEY

c. INSERT KIRK KEY INTO LOCK ON BREAKER MARKED “FED FROM ETC 	       GENERATOR” IN SWITCH GEAR 11-110-033

d. CLOSE GDP#5 MAIN BREAKER IN SWITCH GEAR 11-110-033 MARKED “FED FROM ETC GENERATOR”

e. CLOSE MAIN BREAKER ON ETC GENERATOR. BREAKER IS LOCATED

f. OPEN CROSS TIE BREAKER LOCATED IN SWITCH GEAR 11-110-031 UNDER         ETC GEN SET CONTROL PANEL

g. CLOSE CARVER GENERATOR #1 MAIN BREAKER

6. Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS CLOSED.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July1, 1995

Date Revised: 	July 1, 2013, July 1, 2016

Date Reviewed: July 7, 2016