| SUBJECT/TITLE: | West Colloton Pavilion Diesel Emergency Generator Testing Program |
| --- | --- |
| PURPOSE: | To insure emergency power to West Colloton Pavilion. |

PROCEDURE:

WEST COLLOTON DIESEL EMERGENCY GENERATOR TESTING PROGRAM

THE WEST COLLOTON EMERGENCY GENERATOR SET IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

WEST COLLOTON Emergency Generator is a Caterpillar Generator set, operating at 277/480 Volts, and is located in room JCP 0695-SB

TEST RUN TIME 1 HOUR

1.	Notify Swiss Log desk that generator testing is taking  place. Once tube system is cleared testing can continue.

2.	Check the OIL Level and the Radiator Coolant Level of the engine, if either are low add  to bring

up to proper operating levels. The Coolant level can be checked  in JPP 0762-X-2.Fill out fuel tracking form.

3.	Start generator room exhaust fans in MCC #1 in JCP 0695-SB

4.	Start the Diesel generator set, located in JCP-0695A-SB,  by putting either a critical or life safety switch in the bypass position and turning test switch to TEST position.The emergency power should be available within 10 seconds. DO NOT TURN GENERATOR CONTROL CABINET SELECTOR SWITCH AWAY FROM AUTOMATIC

5.	OPEN THE NORMAL BREAKER FEEDING ATS #14 in switch gear NDP#4 Section #5 Breaker #1 (Located  in JCP 0595-SB)

6.	CHECK THE RADIATOR FANS, LOCATED JPP 0762-X-2

7.	CHECK THE TWO GLYCOL PUMPS LOCATED IN JCP 0595 OUTSIDE THE SOUTH GENERATOR ROOM DOORS. MAKE SURE ONE OF THE PUMPS IS RUNNING. PUMPS ALTERNATE, SO ONLY ONE WILL BE RUNNING.

8.	CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR

CONTROL CABINET FOR THE CORRECT VOLTAGE (480) FOR THE GENERATOR OUTPUT.

9.	Open the NORMAL POWER BREAKER MARKED FOR LOAD TESTING in the COLLOTON WEST PAVILION SWITCHBOARD NDP-5 JCP 7400-B

1)	Section #2 Breaker #4  ATS #3 11-112-055 IN JCP 7400-B

10.	Open the NORMAL POWER BREAKER MARKED FOR LOAD TESTING in the COLLOTON WEST PAVILION SWITCHBOARD NDP-6 JCP 7400-B

1)	 Section #2 Breaker #6 ATS #5 11-112-074 IN JCP 7400-B.

11.	Check and Test all Auto/Bypass Transfer Switches for Proper Operation.

12.	Check any Air handlers or Pumps that should be running, have them restarted if necessary.

13.	Restart cartlift in JCP 7601-X if necessary

14.	Record the readings from the POWERLOGIC METER in the Generator’s control Cabinet into the Generator’s Log Book

AFTER THE TEST RUN IS COMPLETE

15.	Close the NORMAL POWER BREAKERS MARKED FOR LOAD TESTING in the COLLOTON WEST PAVILION SWITCHBOARDS NDP-6 JCP 7400-B, NDP-5 JCP 7400-B AND NDP-4 JCP 0595-SB.

16.	Check and Verify that all Transfer Switches are back in the Normal Power Positions and there are NO tripped breakers.

17.	Check any Air Handlers or Pumps that should be running are,  have them restarted if necessary.

18.	Let the GENERATOR SET time out and shut down. Generator has 5 minute cool down time.

19.	Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS CLOSED.

20.	Fill out fuel tracking form.

Related and Supporting Documentation

•	Utilities Management Program, Facility Operations Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Facility Operations Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July1, 1995

Date Revised: 	July 1, 2013

Date Reviewed: April 18, 2016