| SUBJECT/TITLE: | Pappajohn Diesel Emergency Generator Testing Program |
| --- | --- |
| PURPOSE: | To insure emergency power to Pappajohn Pavilion. |

PROCEDURE:

JOHN PAPPAJOHN DIESEL EMERGENCY GENERATOR TESTING PROGRAM

THE JOHN PAPPAJOHN EMERGENCY GENERATOR SET  IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

JOHN PAPPAJOHN Emergency Generator  is a DETROIT DIESEL Generator set, operating at 277/480 Volts, and is located in room JPP 0763-SB

TEST RUN TIME 1 HOUR

1.	Notify Swiss Log desk that generator testing is taking place. Once tube system is cleared testing can continue.

2.	Fill out fuel tracking form. Check the OIL Level and the Radiator Coolant Level of the engine, if either    are low, add  to bring up to proper operating levels. The Coolant level can be checked  in Room  JPP

0762-X-1

3.	Start the Diesel generator set, located in JPP 0739-B-1,  by putting either a critical or life safety switch in the bypass position and turning test switch to TEST position.The emergency power should be available within 10 seconds.

4.	Open the NORMAL POWER BREAKER MARKED FOR LOAD TESTING in the PAPPAJOHN PAVILION SWITCHBOARD NDP-2 JPP 0910

1)	Section #3 Breaker #5 ATS#3 11-112-094 in JPP 0910

5.	CHECK THE RADIATOR FANS, LOCATED IN ROOM JPP 0762-X-1, THEY ARE ON A THERMOSTAT, AND MAY NOT BE RUNNING

6.	CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR

CONTROL CABINET FOR THE CORRECT VOLTAGE (480) FOR THE GENERATOR OUTPUT.

7.	MANUALLY TRANSFER MTS #5 11-112-126 located in 0763-B TO EMERGENCY POSITION by toggling switch to the emergency position.

8.	Check and Test all Auto/Bypass Transfer Switches for Proper Operation.

9.	Check any Air handlers or Pumps that should be running,  have them restarted if necessary.

10.	Record the readings from the POWERLOGIC METER in the Generator’s control Cabinet into the Generator’s Log Book

AFTER THE TEST RUN IS COMPLETE

11.	CLOSE THE NORMAL POWER BREAKER MARKED FOR LOAD TESTING in the PAPPAJOHN PAVILION SWITCHBOARD NDP-2 JPP 0910. .Manually transfer MTS #5 11-112-126    located in 0763-B back to the normal power source.

12.	Check and Verify that all Transfer Switches are back in the Normal Power Positions and there are NO tripped breakers.

13.	Check any Air Handlers or Pumps that should be running are,  have them restarted if necessary.

14.	Let the GENERATOR SET time out and shut down. There is no cool down timer on gen set.

15.	Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS CLOSED.

16.	Fill out fuel tracking form.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Facility Operations Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July1, 1995

Date Revised: 	July 1, 2013

Date Reviewed: April 18, 2016