| SUBJECT/TITLE: | Emergency Trauma Center Emergency Generator |
| --- | --- |
| PURPOSE: | To ensure emergency power to the Trauma Center. |

EMERGENCY TRAUMA CENTER DIESEL EMERGENCY GENERATOR TESTING PROGRAM

THE EMERGENCY TRAUMA CENTER EMERGENCY GENERATOR SET IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

EMERGENCY TRAUMA CENTER Emergency Generator is a Caterpillar Generator set, operating at 277/480 Volts, and is located in room RCP 0086-SB

TEST RUN TIME: 1 HOUR

A. TEST LOAD TIME: 40 MINUTES

1. Check the OIL Level and the Radiator Coolant Level of the engine, if either are low add  to bring up to proper operating levels. The Coolant level can be checked from the radiator surge tank located in RCP 0086-5

2. Use the load bank to load generator. A 300 KW load is required. Check settings on load bank.

Make sure the motor power selector switch is set to “INT 480”. The voltage toggle switch

should be set to 480.

3. Load bank is connected  to GDP#5 Breaker #2 located in RCP 0086-SB

4. Start the Diesel generator set, located in RCP 0086-SB, by putting either a critical or life safety switch in the bypass position and turning test switch to TEST position. The emergency power should be available within 10 seconds.  Turn selector switch on the Emergency Generator control cabinet in RCP 0086-SB to

RUN within 5 minutes after test is done.

5. CHECK THE RADIATOR FANS, LOCATED IN RCP 0086-5, THAT THEY ARE RUNNING

6. CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR

7. Check and Test all Auto/Bypass Transfer Switches for Proper Operation. The ATS EQ switch is an inhibited switch. Follow the directions on the switch to test.

8. At the load bank, turn “POWER ON”. Check load bank rotation by turning blower on. Air

should move upward from load bank. If rotation is backward turn off blower and wait for

blower to stop. Switch rotation using toggle and restart blower

9. Once rotation is correct turn “MASTER LOAD” toggle to “ON”.

10. Add load to generator by using toggles switches. Add 50 KW at a time until you have a load             of 300 KW.

11. Record the readings from the POWERLOGIC METER in the Generator’s control Cabinet into the

Generator’s Log Book

B. AFTER THE TEST RUN IS COMPLETE

1. Unload generator by toggling the KW load to off. One toggle at a time. When all toggles are     off you can turn off “Master Load” Leave blower running until air above load bank cools to a

comfortable temperature. Usually ONE minute is enough

2. Check and Verify that all Transfer Switches are back in Normal Power Positions and there are NO tripped  breakers.

3. Turn the Selector switch on the Generator Control Cabinet back to AUTOMATIC POSITION.

4. Let the GENERATOR SET time out and shut down. Generator has a one minute cool down timer.

5. Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL

CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS

CLOSED.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

.

Source: UI Healthcare Engineering Services

Date effective: Jan 1, 2000

Date Revised: 	July 1, 2013, July 1, 2016

Date Reviewed: July 7, 2016