# ATTACHEMENT TITLE:		MEDICAL GAS ALARM TEST PROCEDURE

ATTACHMENT NUMBER:		ATT-23

## APPLICABLE POLICY:			C-211

| Instruction Code | 00687 | # Date Last Edited | 11/ 5/2004 |
| --- | --- | --- | --- |

MEDICAL GAS ALARM TEST PROCEDURE – ROY CARVER PAVILION

1. TO TEST MEDICAL GAS ALARMS, PUSH THE TEST BUTTON MODULE READING TEST.

ALL MODULES SHOULD LIGHT UP AND ALARM SOUND.IF BULBS ARE BURNT OUT, REPLACE

WITH CORRECT COLOR BULBS. A SPECIAL TOOL IS NEEDED FOR CHANGING BULB. WHEN

REPLACING BULBS, INSURE THAT ONLY ONE MODULE  AT A TIME IS REMOVED, AS MODULE

CAN BE INTERCHANGED AND AN INNCORRECT SIGNAL WOULD BE GIVEN. (EXAMPLE: LOW

PRESSURE INSERTED ON HIGH PRESSURE SIDE AND VICE/VERSA) IF ALARM DOES NOT SOUND,

NOTIFY YOUR SUPERVISOR. IF UNIT HAS GUAGES, INSURE THAT THE GUAGES ARE IN

OPERATING RANGE. IF NOT IN OPERATING RANGE, REPORT TO YOUR SUPERVISOR.

LOCATIONS:

| RCP-1100-1 | RCP-5046 |
| --- | --- |
| RCP-2088 NSS | RCP-5065 NSS |
| RCP-2089 NSS | RCP-5070 NSS |
| RCP-2061 NSS | RCP-5102 NSS |
| RCP-2108 NSS | RCP-5110 NSS |
| RCP-3173-Z NSS | RCP-6061 NSS |
| RCP-3227 HALLWAY | RCP-6089 NSS |
| RCP-3088 NSS | RCP-6109 NSS |
| RCP-3089 NSS | RCP-6248 NSS |
| RCP-3108 NSS | RCP-7089 S. NSS |
| RCP-3201-1 HALLWAY | RCP-7061 N. NSS |
| RCP-4089 NSS |  |
| RCP-4062 NSS |  |
| RCP-4006 NSS |  |
| RCP-5091 NSS |  |
| RCP-5086 HALLWAY |  |