# ATTACHEMENT TITLE:		MEDICAL GAS ALARM TEST PROCEDURE

ATTACHMENT NUMBER:		ATT-25

## APPLICABLE POLICY:			C-211

| Instruction Code | 00896 | Date Last Edited | 11/ 5/2004 |
| --- | --- | --- | --- |

MEDICAL GAS ALARM TEST PROCEDURE – JOHN PAPPAJOHN PAVILION

1. TO TEST MEDICAL GAS ALARMS, PUSH THE TEST BUTTON MODULE READING TEST.

ALL MODULES SHOULD LIGHT UP AND ALARM SOUND. IF BULBS ARE BURNT OUT, REPLACE

WITH CORRECT COLOR BULBS. A SPECIAL TOOL IS NEEDED FOR CHANGING BULB. WHEN

REPLACING BULBS, INSURE THAT ONLY ONE MODULE  AT A TIME IS REMOVED, AS MODULE

CAN BE INTERCHANGED AND AN INNCORRECT SIGNAL WOULD BE GIVEN. (EXAMPLE: LOW

PRESSURE INSERTED ON HIGH PRESSURE SIDE AND VICE/VERSA) IF ALARM DOES NOT SOUND,

NOTIFY YOUR SUPERVISOR. IF UNIT HAS GUAGES, INSURE THAT THE GUAGES ARE IN

OPERATING RANGE. IF NOT IN OPERATING RANGE, REPORT TO YOUR SUPERVISOR.

LOCATIONS:

| JPP-0732 PHYSICAL THERAPY | JPP-6772 |
| --- | --- |
| JPP-0751 NSS CLINIC EAT | JPP-6780 NSS |
| JPP-0795 X-RAY | JPP-6816 |
| JPP-0775-2 CLINICS A & B | JPP-6817 NSS (2) |
| JPP-0824 P.E.T. AREA | JPP-6826 HALL (2) |
| JPP-1911 ADULT PSYCH CLINIC NSS | JPP-6831 |
| JPP-1804-Z NEUROSURGERY CLINIC | JPP-6851 |
| JPP-3RD FL NSS EAST & WEST | JPP-6853 |
| JPP-3820 NSS NUCLEAR MEDICINE | JPP-6868 |
| JPP-4708 HALLWAY AT NSS, EAT & WEST | JPP-6869 |
| JPP-4970-2 NSS CHEMOTHERAPY | JPP-6870 |
| JPP-4817 MED. PREP. ROOM | JPP-6920-Z |
| JPP-5866 HYPERBARIC | JPP-6933 |
| JPP-5730-Z ICU BAY 1 | JPP-6935-Z |
| JPP-5740-Z ICU BAY 2 | JPP-6937 |
| JPP-5750-Z ICU BAY 3 | JPP-6951 NSS (2) |
| JPP-5770-Z ICU BAY 4 | JPP-6954 |
| JPP-6719 NSS | JPP-6957 |
| JPP-6721 | JPP-6956 |
| JPP-6735 | JPP-7731-1 |
| JPP-6738 HALLWAY | JPP-7737 |
| JPP-6742 | JPP-7746 |
| JPP-6767 NSS | JPP-7761 |
|  | JPP-7782 |