# ATTACHEMENT TITLE:		MEDICAL GAS ALARM TEST PROCEDURE

ATTACHMENT NUMBER:		ATT-26

## APPLICABLE POLICY:			C-211

| Instruction Code | 00897 | Date Last Edited | 11/ 5/2004 |
| --- | --- | --- | --- |

MEDICAL GAS ALARM TEST PROCEDURE – POMERANTZ FAMILY PAVILION

1. TO TEST MEDICAL GAS ALARMS, PUSH THE TEST BUTTON MODULE READING TEST.

ALL MODULES SHOULD LIGHT UP AND ALARM SOUND. IF BULBS ARE BURNT OUT, REPLACE

WITH CORRECT COLOR BULBS. A SPECIAL TOOL IS NEEDED FOR CHANGING BULB. WHEN

REPLACING BULBS, INSURE THAT ONLY ONE MODULE  AT A TIME IS REMOVED, AS MODULE

CAN BE INTERCHANGED AND AN INNCORRECT SIGNAL WOULD BE GIVEN. (EXAMPLE: LOW

PRESSURE INSERTED ON HIGH PRESSURE SIDE AND VICE/VERSA) IF ALARM DOES NOT SOUND,

NOTIFY YOUR SUPERVISOR. IF UNIT HAS GUAGES, INSURE THAT THE GUAGES ARE IN

OPERATING RANGE. IF NOT IN OPERATING RANGE, REPORT TO YOUR SUPERVISOR.

LOCATIONS:

PFP-01245

PFP-01250

PFP-11123-B

PFP-21113

PFP-51335-1, NURSE STATION