ATTACHEMENT TITLE:		STEAM REGULATOR PRESSURE

ATTACHMENT NUMBER:		ATT-17

## APPLICABLE POLICY:			C-205

| ### BUILDING / FLOOR / ROOM | ### HIGH PRESSURE (PSI) | ### MEDIUM PRESSURE ### (PSI) | ### LOW PRESSURE ### (PSI) |
| --- | --- | --- | --- |
| Boyd Tower Lower Level BT0037 | 150 to 160 | 60 to 70 | 5 to 20 |
| General Hospital Lower Level B23 | 90 to 120 | 50 to 65 | 5 to 20 |
| General Hospital (West - PEDS) Lower Level W196 | 150 to 160 | NA | 5 to 20 |
| General Hospital (West - RAD) Lower Level W1 | NA | NA | 5 to 20 |
| South Wing Lower Level S12 | 80 to 90 | 25 to 55 | 5 to 20 |
| Carver (West) 7th Floor Penthouse 7710 | 150 to 160 | 40 to 70 | 5 to 20 |
| Carver (East) Lower Level 2 0086 | 150 to 160 | 40 to 55 | 5 to 20 |
| Carver (West) 0295 Lower Level 2 | 150 to 160 | 40 to 55 | 5 to 20 |
| Colloton (East) Lower Level 2 0350 | 150 to 160 | 40 to 55 | 5 to 20 |
| Colloton (West) Lower Level 2 0495 | 150 to 160 | 40 to 55 | 5 to 20 |
| Pappajohn (East) Lower Level 2 0700 | 150 to 160 | 50 to 65 | 5 to 20 |
| Pappajohn (West) Lower Level 2 0895 | 150 to 160 | 50 to 65 | 5 to 20 |
| Pomerantz Lower Level 3 00003 | 150 to 160 | 50 to 65 | 5 to 20 |