| SUBJECT/TITLE: | Power Outage Procedure after Normal Hours |
| --- | --- |
| PURPOSE: | To maintain operation of Electrical Systems |

PROCEDURE:

The first thing to remember is to stay calm and do your job.  If you act nervous or unsure of yourself, you will make the staff in the area of the power outage nervous, which can cause an over reaction on their part.  Over reaction on the part of any hospital personnel, from administrators on down, can make your job very difficult.  Patients can become upset, too many people will be giving you orders and telling you how to do your job electrically, which can cause confusion and waste valuable time.  Remember, you must be in control of the situation in order to do you job quickly and correctly.

A. Listed below are some recommended steps to follow in a power outage.  These steps are not meant to be used for individual breakers in area panels.

1.	GO TO ELECTRICAL SYSTEMS METER ROOM

a. Go to the Electrical Systems Office and check the meters and the 			alarm monitoring systems, to see what areas are out of power.

b. Check to see that the Emergency Power Generator is running for the 			area that is without power, and that the transfer switches are in their proper 		position.

2.	LINES OF COMMUNICATION

a. Phone the Telephone Communications Center (Dial 0) to let them 			know you are in the building and are checking out the problem.  Ask 			the operator if anyone has called needing help from the electrician.  			Tell the operator what pager number you are carrying.

b. Also notify 	Security or have the operator call them, so they will know 			you are present in the building and looking into the outage.  Carry a two- 			way radio with the Security channel so you can make direct contact with 			the Security personnel.

3.	NECESSARY TOOLS

a. Get together some basic tools to check the outage area.  A flashlight, 			screwdriver and voltage meter of some type.

4.	OUTAGE AREA

a. Proceed to the area involved in the outage and determine if it is a 			localized outage or an out of the building type outage.

b. If it is localized, such as just a tripped breaker in the switchgear, try to 			reset it.

c. If it is outside the building, you will need to contact the Physical Plant 			High Voltage Distribution Shop at 335-5146 or 331-0512.  Explain what 			building is being affected.

5.	CHECK EMERGENCY GENERATOR SET

a. Check the Emergency Generator set in the outage area.

b. Be sure that the amperage is within proper range of the generator 			nameplate rating and that the engine gauges are reading OK.

c. Check for overheating of the generator and that the generator is 				ventilated.

6.	NOTIFY SUPERVISOR

a. Contact the Electrical Systems Supervisor, Eldon Hanson, or have 			Security contact him to inform him of the outage.

b. If you cannot contact the Supervisor, then contact the Operations 			Manager.

7.	AIR HANDLING EQUIPMENT ON MANUAL TRANSFER SWITCHES

a. Contact the Environmental Systems Shop on-call personnel and let them know 	what areas have the outage.

b. Find out if they are going to need any air	handling equipment that is fed from 	a manual transfer switch placed into service.  This needs to be based on how 	much load is on the Emergency Power Generator.

c. Check the amperage reading of the generator set, and if it is allowable, the 	manual transfer switch may be closed to Emergency Power to power up the air 	handling equipment.  IF THE OUTAGE IS IN EAST COLLOTON 	SWITCHBOARD NDP1 IN ROOM JCP 0350-A MANUAL TRANSFER 	SWITCHES TS-4 11-112-052 LOCATED IN JCP 0350-A NEED TO BE 	TRANSFERRED TO EMERGENCY POWER TO MAINTAIN AIR 	HANDLING FOR AMBULATORY SURGERY CENTER ON 5TH FLOOR 	JCP.

d. When the outage is over, you will need to close these and any other manual 	transfer switches back to Normal Power.

8.	X-RAY EQUIPMENT ON MANUAL TRANSFER SWITCHES

a. If the outage is the normal power to Colloton switchboard NDP4, you 			will need to transfer the manual switch for x-ray equipment.

b. Check the amperage reading on the West Colloton Generator and if allowable, 		close the manual transfer switches to emergency power, to power up 			the x-ray equipment.  These switches are located in JCP 0595-A.  The 			switch numbers and PM numbers are TS-1511-112-066, TS-15A 11-			112-068, TS-17 11-112-069.

c. Notify Diagnostic Radiology at 356-3344 or Radiology Engineering at 356-	3377 or 356-3387 that they are on Emergency Power.

d. When Normal Power is restored, BEFORE YOU TRANSFER X-RAY BACK 	TO NORMAL POWER, again contact Diagnostic Radiology at 356-3344 or 	Radiology Engineering at 356-3377 or 356-3387.

e. Then close the transfer switches back to Normal Power.

9.	NURSING PERSONNEL IN OUTAGE AREA

a. Check with nursing personnel in the outage area to see if they need 			anything to support their area, such as drop cords or flashlights.

10.	EXTERIOR DISTRIBUTION SYSTEM OUTAGE

a. If it is an exterior distribution system outage, as in step number 4, you 			will need to check with the Physical Plant personnel to get better 				details of what will be the extent, and approximate length of time for 			the outage.

b. Make sure this information is reported to the Electrical 				Systems Supervisor, the Crafts Manager and the Work Control Center.

11.	OUTAGE DATA COMPLETION

a. When the power outage is over and all Normal power is restored and 			the Emergency Power Generators are shut down, the generator log 			books need to be filled out and all items noted in them.

b. A utility outage form needs to be filled out completely.  The utility outage 	forms are in the Electrical Craft Shop.

Remember, these procedures may not be able to be followed in this exact order in all outage situations.  Every power outage is a little different.  It depends greatly on the area that is out, the people working in that area, the severity of the outage and the length of time involved.  The main thing to remember is to stay calm and do your job to the best of your ability.

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: August 20, 2008, July 1, 2016

Date Reviewed: July 20, 2016