| SUBJECT/TITLE: | Pomerantz Diesel Emergency Generator #1 |
| --- | --- |
| PURPOSE: | To insure emergency power to the Pomerantz Pavilion. |

PROCEDURE:

POMERANTZ PAVILION DIESEL EMERGENCY GENERATOR #1 TESTING PROGRAM

THE POMERANTZ PAVILION EMERGENCY GENERATOR SET #1 IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

POMERANTZ PAVILION Emergency Generator #1 is a Caterpillar Generator set, operating at 277/480 Volts, and is located in room PFP 00002-SB

TEST RUN TIME 1 HOUR

1.	Check the OIL Level and the Radiator Coolant Level of the engine, if either are low, add  to bring

up to proper operating levels. The Coolant level can be checked from the radiator in PFP 00154-

1.	Start the PFP #1Diesel generator set, located in PFP 00002-SB, by putting either a critical or life safety switch in the bypass position and turning test switch to TEST position. The emergency power should be available within 10 seconds.  After the generator is running, turn selector switch on generator control cabinet to RUN.

2.	CHECK THE OPERATING VOLTAGE ON THE POWERLOGIC METER IN THE GENERATOR CONTROL CABINET FOR THE CORRECT VOLTAGE FOR THE GENERATOR OUTPUT.

3.	Transfer TS-M6 11-112-138 located in PFP 00005 to Emergency Power.

4.	Put TS-M2 in the manual position and transfer to Emergency Power.

5.	Check any Air handlers or Pumps that should be running, have them restarted if necessary.

6.	CHECK THE RADIATOR FANS, LOCATED PFP 00154-Y, THAT THEY ARE RUNNING

7.	Check and Test all Isolate/Bypass Transfer Switches for Proper Operation.

8.	Record the readings from the POWERLOGIC METER in the Generator’s control Cabinet into the Generator’s Log Book

AFTER THE TEST RUN IS COMPLETE

9.	Transfer TS-M6 (11-112-138) and TS-M2 (11-112-134) located in PFP 00005 to Normal Power.

10.	Return TS-M2 (11-112-134) to the automatic position.

11.	Return selector switch on generator control cabinet to automatic. Gen set should shut down after TS-M2 times out(5 min.).

12.	Check and Verify that all Transfer Switches are back in there Normal Power Positions and there are NO tripped breakers.

13.	Check any Air Handlers or Pumps that should be running are,  have them restarted if necessary.

14.	Let the GENERATOR SET time out and shut down. Should shut down 5 minutes after transfer switch TS-M2(11-112-134) transfers to normal.

Fill out all Generator Log Book entries and MAKE SURE THAT THE GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC POSITION AND MAIN BREAKER IS CLOSED.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

.

Source: UI Healthcare Engineering Services

Date effective: March 1, 1996

Date Revised: 	July 1, 2013

Date Reviewed: April 18, 2016