| SUBJECT/TITLE: | Center for Disabilities and Development Diesel Emergency Generator Testing Program |
| --- | --- |
| PURPOSE: | To ensure emergency power to CDD. |

CENTER FOR DISABILITIES AND DISEASE DIESEL EMERGENCY 
GENERATOR TESTING PROGRAM

THE CDD EMERGENCY GENERATOR SET IS TO BE TESTED ONCE A MONTH UNDER LOAD AS PER CODE AND ESTABLISHED STANDARDS FOR TESTING.

CDD Emergency Generator is a Cummins Generator Set, operating at 120/208 Volts. It is located in Room CDD M2.

A. RUN TIME 1 HOUR

1. Check the OIL Level and the Radiator Coolant Level of the engine, if either are low, add to bring up to proper operating levels. The coolant level can be checked in CDD M2, surge tank located in ceiling, remove cap and use dip stick to measure level.

2. Start the Diesel generator set, located in CDD M2,  by opening the normal breaker feeding ATS-2, 11-112-128, located in NDP #1 Section 3 Breaker 10, CDD 127A,  thus initiating a complete cold start. The emergency power should be available within 10 seconds.

3. Once the generator is running, Open the NORMAL POWER BREAKERS MARKED FOR LOAD TESTING in the CDD SWITCHBOARD NDP-1 ROOM CDD 127A.

Section #4 Breaker #7 ATS-3 11-112-129

Section #5 Breaker #1 ATS-1 11-112-127

4. Verify that all (3) transfer switches in room 124 have transferred

5. Turn selector switch on the Emergency Generator control cabinet to RUN.

6. CHECK THE RADIATOR FAN LOCATED IN ROOM, VERIFY IT IS RUNNING.

7. CHECK THE OPERATING VOLTAGE ON THE METER ON THE GENERATOR CONTROL CABINET, VOLTAGE SHOULD BE 208 VOLTS~.

8. Check any Air Handlers or Pumps that should be running are, have them restarted if

necessary.

9. Record the readings from the METER, in the Generator’s Control Cabinet into the

CDD Generator’s Log Book

10. Close all (3) of the NORMAL POWER BREAKERS MARKED FOR LOAD

TESTING in the CDD SWITCHBOARD NDP-1 ROOM CDD 127A

11.Check and Verify that all Transfer switches are back in Normal Power Positions and

there are no tripped Breakers, including the Main Breaker on Generator.

12. Check that any Air Handlers or Pumps that should be running are, have them

restarted if necessary.

13.	Turn the selector Switch on the Generator Control Cabinet to the AUTOMATIC

POSITION.

14. Let the CDD GENERATOR SET time out and shut down.

15. Fill out all Generator Log Book entries and MAKE SURE THAT THE

GENERATOR CONTROL CABINET SELECTOR SWITCH IS IN THE AUTOMATIC

POSITION AND THE GENERATOR MAIN BREAKER

IS CLOSED.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: 	July 1, 2013, July 1, 2016

Date Reviewed: July 7, 2016