| SUBJECT/TITLE: | Medical Air System/Vacuum Emergency Procedures |
| --- | --- |
| PURPOSE: | To restore Med Air system. |

A.	Engineering Services On-Call Personnel will:

1. Open cross-tie valve to system operation.

2. Locate source of problem and make repairs as necessary.

3. Call in additional personnel, if needed.

4. Activate emergency call list, if needed.

B.	If repairs cannot be made in a reasonable amount of time (30 minutes or less),

Engineering Services will notify the following:

1. Safety and Security

2. Department of Respiratory Care

3. Nursing

4. Effected Area.

C.	Respiratory Care will provide compressors or portable tanks of compressed gas for the most oxygen sensitive patients and determine the need for portable compressed gas throughout the hospital.  Place all respiratory care requirements on a priority basis.

D.	The Director of Respiratory Care shall be responsible for ordering additional Medical Air Supplies until the failure has been corrected, and purity test made, (If required).

E.	Nursing will closely monitor and support patients during the interim period.  Be prepared to relocate patients.

F.	In the event the main supply line has ruptured, Activate Emergency Call list (attached).  Engineering Services Supervisor will request Outside Contractor, if needed.

G. Related and Supporting Documentation

1. Utilities Management Program, Engineering Services Policy C-001

2. Safety Reference Cards

3. On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July1, 1995

Date Revised: July 1, 2013

Date Reviewed: April 13, 2016