| SUBJECT/TITLE: | Bulk Medical Gas Storage Facility Emergency Procedures |
| --- | --- |
| PURPOSE: | To restore medical gas system failure. |

Safety and Security will notify Engineering Services On-Call Personnel.  Safety and 	Security will notify Engineering Services Supervisor.

1 	Engineering Services On-Call Personnel will:

A.	Open cross-tie valve to get building back in operating status

B.	Locate source of problem and make repairs as necessary

C.	Call in additional personnel, if needed

D.	Activate Emergency Call List, (attached) if needed.

2.	If repairs cannot be made in a reasonable amount of time (30 minutes or 			less), Engineering Services will notify the following:

A.	Safety and Security

B.	Department of Respiratory Care

C.	Nursing

D.	Emergency Area

E.	Operating Rooms Area

3.	In the event the main supply line has ruptured, activate Emergency Call list 		(attached).  Engineering Servcies Supervisor will request Outside Contractor, 		if needed.

4.	Lay-out - Main and Reserve Systems:

A.	The equipment consists of a main bulk liquid oxygen tank, 					6,400 gallon, with a capacity of 275 inches of product which is a 				26 day supply.  Deliver line pressure is 58 PSI.

B.	The reserve system consists of a bulk liquid oxygen tank, 600 				gallon, with a capacity of 90 inches of product which is a 9 day 				supply.  Should a malfunction occur or the main tank supply is 				depleted, automatic switch over to the reserve system occurs.  				A secondary regulator is built into the system.  If the main 					regulator malfunctions, manual switch over can be 						accomplished in a matter of minutes.

5.	Emergency Supply:

A. In the event that both the main and reserve systems should fail, 				     oxygen tanks would be supplied by Hospital Stores, General 				     Stores, and all other available Hospital personnel.  A tanker will 			     be dispatched immediately to arrive no later than 24 hours after 		         		     the call.  The tanker would be hooked to the oxygen supply 				     system.  Oxygen would be pumped directly from the tanker 				      into the Hospital pipeline, located in the East corner of the 				     Shipping and Receiving Facility.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July1, 1995

Date Reviewed: April 14, 2016