| SUBJECT/TITLE: | Medical Gas Alarm Panel Building and Equipment Maintenance Management Testing Procedure and Failure Procedure |
| --- | --- |
| PURPOSE: | To test and maintain Med Gas Alarm. |

PROCEDURE:

For Building and Equipment Maintenance Management Testing Procedures, see Attachments.

PROCEDURE:

Failure Procedure:

1. Engineering Services On Call Personnel will:

A. Open cross-tie valve to system operation.

B. Locate source of problem and make repairs 						     as necessary.

C. Call in additional personnel, if needed.

D. Activate emergency call list, if needed.

2. If repairs cannot be made in a reasonable amount of time (30 minutes or less), Engineering Services will notify the following:

A. Safety and Security

B. Respiratory Care Department

C. Nursing

D. Effected Area

3. Respiratory Care will provide compressors for the most 	oxygen sensitive patients and determine the need for portable compressors throughout the hospital.  Place all respiratory care requirements on a priority basis.

4. The Director of Respiratory Care shall be responsible for ordering additional Medical Air Supplies until the failure has been corrected, and purity tests made (if required).

5. Nursing will closely monitor and support patients during 					the interim period.  Be prepared to relocate patients.

6. In the event the main supply line has ruptured, activate 				     	Emergency Call list (attached).   Engineering Services 					Supervisor will request Outside Contractor, if needed.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: July 1, 2001

Date Reviewed: April 19, 2016