| SUBJECT/TITLE: | Failure of Air Handling Unit |
| --- | --- |
| PURPOSE: | To maintain operation of Air Handler units. |

A. PROCEDURE:

1. ATTENTION:  For Failure of the Air Handling Units listed below, refer to policies in this section with specific instructions relative to each unit.  Failure to follow instructions could put patients and or staff at risk.

a. Air Handling Units # 13 and # 14 RCP (Bone Marrow Transplant), see Policy 		    # C303.

b. Air Handling Units # 18 through # 22 JCP (Operating Rooms), see Policy  		    # C307.

c. Air Handling Unit # 1 JPP (P.E.T.), see Policy # C308

d. Air Handling Unit # 20 GH (Invitro Fertilization and Labor and Delivery), see 		    Policy # C302.

e. Air Handling Unit # 16  and# 23 JCP (CSS), see Policy # C306.

f. Air Handling Units # 6 and # 7 JCP (MORE), see Policy # C304.

g. Air Handling Unit # 11 JCP (M.R.I.), see Policy # C305.

h. Air Handling Units # 3 and # 6 JPP (Nuclear Medicine), see Policy # C309.

i. Air Handling Units # 12, 13 and 14 JPP (S.I.C.U.), see Policy # C310.

B. For all other Air Handling Units, check for the following:

1.	Control Failure

a. If connected to a Building Automation System, check monitoring 			     screen at operator work station for unit status, alarms, on/off 				scheduling, etc.  If not connected to a Building Automation 					System, check the control panel at the Air Handling Unit.

b. Check the safety controls (low limit, static pressure, damper 					switch).

c. Check for twenty pound main control air at control panel.  If 				     main air pressure is low or zero, refer to Policy # C318, Failure 				     Control Air.

C. Electrical Failure

1. Check thermal overloads, fuses and or breakers.

D. Mechanical Failure

1. Check belts, bearings, damper linkage, actuator diaphragms, 				                       	control air lines, etc.

E. Notify the area(s) served as to the status of the Air Handling Unit and the 			length of time required to effect repairs for their planning purposes.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Reviewed: April 19, 2016