| SUBJECT/TITLE: | Failure of Scheduled Shutdown of RCP Air Handling Units 13 and 14 serving the Bone Marrow Transplant Units |
| --- | --- |
| PURPOSE: | To maintain operation of Air Handler units #13 and #14. |

A.  PROCEDURE:

1.  WARNING:  Notify Adult and Pediatric Bone Marrow Transplant units prior to      	scheduled shut down, as soon as possible after unscheduled shutdown, and prior 	to start-up.  Failure to notify puts patients at risk.

B.	Notification

1. If either unit is found out of service for unplanned reasons, the charge nurse on each unit must be notified immediately.  For a planned shutdown (scheduled maintenance or repairs), the charge nurse on each unit must be notified before turning the air-handling unit off.  Proper notification requires you to complete a Bone Marrow Transplant Unit Air Handling Unit Interruption Notice.  The blank forms can be found in the RCP 8th Floor equipment room (RCP 8051), or in the Environmental Systems Shop.

C.	Completing Interruption Notice Form

1. A separate notice is required for each nursing unit.

2. Indicate which air-handling unit is or will be out of service by 				marking the form next to the area(s) served.  The inpatient 					rooms are served by AHU 14 and the interior service core plus 				inpatient rooms 7043 through 7047.  Rooms 7091 through 7095 				are served by Air handling unit 13.

3. Indicate the Air Handling Unit is out of service (unplanned) or 				will be out of service.  For scheduled service fill in date and 					time of shutdown.

4. Indicate when the Air Handling Unit will be back in service by 				filling in the date and approximate time the work will be 					completed.

5. Indicate reason for outage.  (Off on low limit trip, scheduled 					maintenance, etc.).

6.	Fill in contact name and phone number in case nursing unit 	staff have any 	questions.

D.	Interruption Notification

1. Indicate if Adult or Child unit is being notified.

2. Have Charge Nurse sign on line AA and fill in date and time.

3. Remove pink copy and give to the Charge Nurse.

4.	Shut off Air Handling Unit and complete required maintenance or repairs.

E.	Unit Back in Service Notification (prior to start-up)

1. Have Charge Nurse sign on line BB and fill in date and time.

2. Ask Charge Nurse how much time will be required to mask the 				patients before starting the Air Handling Unit(s).

3. Remove yellow copy and give to the Charge Nurse.

4. Wait the required length of time before starting the Air Handling 				Unit(s).

5. Return original copy to the Facilities Shop.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: Aug. 6, 2001

Date Reviewed: April 19, 2016