| SUBJECT/TITLE: | Failure of MORE Air Handling Units #6 and #7 JCP |
| --- | --- |
| PURPOSE: | To maintain operation of Air Handler units #6 and #7 JCP. |

A. PROCEDURE:

1.	Notify staff in MORE area at 356-0500 about the failure and the areas affected.

2.	Check affected Air Handling Unit for the following:

a. Control Failure

1. Check pneumatic - electric switch.  Compressor is 					     located in JPP West basement.

2. Check operation of unit on Johnson Controls Computer 					     System.

b.	Electrical Problems

1. Check thermal overloads, fuses, and or breakers.

c.	Mechanical Failure

1. Check belts, bearings and motors.

3.	If Environmental Systems Mechanic is unable to identify the problem, contact the 	lead person, Engineering Services and the Director of Engineering Services as 	required.

4.	Notify the staff in MORE at 356-0500 as to the status of the Air 		Handling Unit and the length of time required to effect repairs for their 			planning purposes.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: Aug. 8, 2001

Date Reviewed: April 19, 2016