| SUBJECT/TITLE: | Failure of CSS Air Handling Units #16 and #23 JCP |
| --- | --- |
| PURPOSE: | To maintain operation of Air Handler units #16 and #23 JCP. |

A. PROCEDURE:

1.	Notify staff in CSS JCP area at 356-2534 about the failure and the areas 			affected.

2.	Check the affected Air Handling Unit for the following:

a. Control Failure

1. Check the pneumatic -- electric switch.  The compressor 					is located in JPP West basement.

2.	Check the operation of unit on Johnson Controls 						Computer System.

b. Electrical Problems

1. Check thermal overloads, fuses and or breakers.

c. Mechanical Failure

1. Check belts, bearings and motors.

3.	Check affected exhaust fans the same as listed above.

4.	If Environmental Systems Mechanic is unable to identify the problem, contact the 	lead person, Operations Manager of Engineering Services and the Director of 	Engineering Services, as required.

5.	Notify staff in CSS Department at 356-2534 as to the status of the Air 	Handling Unit and the length of time required to effect repairs for their planning 	purposes.

Related and Supporting Documentation

Utilities Management Program, Engineering Services Policy C-001

Safety Reference Cards

On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: Aug.10, 2001

Date Reviewed: April 19, 2016