| SUBJECT/TITLE: | Failure of Operating Room suite Air Handling Units #18 - #22 |
| --- | --- |
| PURPOSE: | To maintain operation of Air Handler units #18 - #22. |

A. PROCEDURE:

1.  Notify staff in Operating Room Department by contacting the OR Charge 			Nurse at 356-6400 of the failure and the areas affected.

2.  Check the affected Air Handling Unit for the following:

a. Control Failure

1. Check pneumatic -- electric switch.  Compressor is 						located in JCP 7400-C.

2. Check operation of unit on Siemens BAS

b. Electrical Problems

1. Check VFD for power.

2. If no power to VFD, check breaker located in JCP 7400-A.

c. Mechanical Failure

1. Check motor and fans (fan array)

3.  If Environmental Systems Mechanic is unable to identify the problem, contact the 	lead person, Operations Manager of Engineering Services and the Director of 	Engineering Services as required.

4.  Notify staff in Operating Room Department at 353-6400 as to the status of 		the Air Handling Unit and length of time required to effect repairs for their 		planning purposes.

5.  If the Operating Room schedule is going to be affected, notify the Operations 	Manager of Engineering Services and the Director of Engineering Services.

6.  Complete a Utility Interruption Report and submit it to the Operations Manager of 	Engineering Services.

Related and Supporting Documentation

•	Surgical Services Emergency Preparedness Plan

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

•	Surgery Suite Communications for Utility Interruption, Engineering Services

Policy C-002

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: Aug.10, 2001

Date Reviewed: April 20, 2016