| SUBJECT/TITLE: | Failure of Positron Emission Tomography Air Handling Unit #1 JPP and or Exhaust Fans |
| --- | --- |
| PURPOSE: | To maintain operation of Positron Emission Tomography (PET) Air Handler unit #1 |

A. PROCEDURE:

1.	Notify the staff in the P.E.T. Area at 356-4100 about the failure and the areas 		that will be affected.

2.	Check the affected Air Handling Unit for the following:

a. Control Failure

1) Check the pneumatic - electric switch.

2) Check the operation of the unit on the Johnson 					          	     Controls computer system.

b. Electrical Problems

1) Check the disconnect for power

c. Mechanical Failure

1) Check belts, bearings and motors.

3.	If the Environmental Systems Mechanic is unable to identify the problem, 			contact the lead person, Operations Manager of Engineering Services and 		the Director of Engineering Services, as required.

4.	Notify the staff in the P.E.T. Area at 356-4100 as to the status of the Air 			Handling Unit and the length of time that will be required to effect repairs for 		their planning purposes.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services  Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: Aug.10, 2001

Date Reviewed: April 19, 2016