| SUBJECT/TITLE: | Failure of SICU/Perinatal Air Handling Units #12- #16 JPP |
| --- | --- |
| PURPOSE: | To maintain operation of SICU/Perinatal Air Handlers #12-#16. |

A. PROCEDURE:

1.	Notify the staff in SICU JPP area at 356-4141 and/or in the Perinatal area at 356-	2631 about the failure and the areas affected.

2.	Check the affected Air Handling Units for the following:

a. Control Failure

1. Check the pneumatic - electric switch

2. Check the operation of the unit on Johnson Controls and Siemens computer 			systems.

b. Electrical Problems

1. Check thermal overloads, fuses and or breakers.

c. Mechanical Failure

1. Check belts, bearings and motors.

3. Check affected exhaust fans in the same manner as listed above.

4. If the Environmental Systems Mechanic is unable to identify the problem, contact the lead person, Operations Manager of Engineering Services and the Director of Engineering Services, as required.

5. Notify the staff in the SICU Department at 356-4141 and/or in the Perinatal area at 356-2631as to the status of the Air Handling Unit and the length of time required to effect repairs for their planning purposes.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Source: UI Healthcare Engineering Services

Date effective: July 1, 1995

Date Revised: Nov. 2, 2004

Date Reviewed: April 19, 2016