| SUBJECT/TITLE: | Failure of Control Air |
| --- | --- |
| PURPOSE: | To maintain operation of control air. |

A. PROCEDURE:

1. Failure of a control air system may cause a shut-down of critical equipment in the 	area served.  Refer to policies in this section with instructions relative to a specific 	piece or type of equipment.  Failure to follow instructions could put patients or 	staff at risk.

2.	Control Failure

a. Check pneumatic-electric switch.

b. On dual compressor models, check alternator switch.

3.	Electrical Failure

a. Check thermal overloads, fuses and or breakers.

4.	Mechanical Failure

a. Check belts and bearings, piping for leaks, pressure regulator.

b. Check compressor(s) performance for signs of internal damage.

5.	Drier Failure

a. If water is present in the pneumatic piping, check the performance of 			     the drier.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Revised: July 27, 2001

Date Reviewed: April 21, 2016