| SUBJECT/TITLE: | Failure of Water Pump |
| --- | --- |
| PURPOSE: | To maintain operation of water pump. |

A. PROCEDURE:

1.	Control Failure

a. If connected to a Building Automation System, check the 				     monitoring screen at operator workstation for pump status and 				     alarms.  If it is not connected to a Building Automation System, 			     check the motor starter or variable speed drive at the pump.

b. Ensure there is control power to the motor starter coil or control 			         signal to VSD.

2.	Electrical Failure

a. Check thermal overloads, fuses and or breakers.

b. Check VSD for fault condition.

3.	Mechanical Failure

a. Ensure that the pump shaft coupling is in good condition and 				     pump is rotating.

b. Ensure that bearings and seals are in good condition.

4.	Flow Failure

a. Ensure pump strainer is clean.

b. Ensure pump differential pressure is within proper limits.

c. Ensure system pressure or water volume is correct.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 21, 2016