| SUBJECT/TITLE: | Failure of Operating Rooms Chilled Water Backup Cooling Change Over |
| --- | --- |
| PURPOSE: | To maintain operation of Operating Rooms chilled water. |

A. PROCEDURE:

1.	Check main chilled water pumps (Pumps 18, 19, and 20) located across from 		Air Handling Unit # 11 in JCP West Basement.

2.	If JCP system is down, switch chilled water supply from JCP West Basement 		pumps to JPP West Basement pumps.

3.	The valves are located in the 7th floor equipment room, by the chilled water 		header, between the large condenser blower units.  There are four 				valves.  To change to JPP chilled water, close two valves tagged (JCP Main 		Chilled Water), and open valves tagged (JPP Main Chilled Water).  Reverse 		the process if changing from JPP to JCP.

4.	Reverse the above processes when main chilled water is restored.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 22, 2016