| SUBJECT/TITLE: | Access to Ceiling Space 7RCP Bone Marrow Transplant |
| --- | --- |
| PURPOSE: | To prevent aspergillus contamination. |

A. PROCEDURE:

WARNING:  Failure to follow these instructions can release aspergillus into hallways and patient rooms.  This fungus is lethal to the Bone Marrow Transplant patient population.  If you have any questions or concerns, contact the Charge Nurse on duty in either Adult or Pediatric Bone Marrow Transplant.

1. Unless an extreme emergency, the ceiling in the hallway should be 			     entered on the evening shift, when the fewest number of patients are 			     in the hallway.  If work must be done in the ceiling of a patient room, or 		     a room patients use (classroom or playroom), the patient(s) must leave 			     the room and all supplies and belongings must be taken out of the 			     room.

2. Plastic barriers- HEPA cart  be put up at all times prior to entering the ceiling.  			    The barrier will be plastic sheeting from ceiling to floor completely 			     enclosing the access area, held in place with duct tape.  Contact 				     Engineering Services Structural Craft Shop (353-6423) between the 			     hours of 7:00 A.M. and 3:30 P.M., Monday through Friday, for barrier 			     installation.  On nights or weekends, the responding mechanic must 			     install the barrier, assisted by other Engineering Services or 				     Housekeeping staff.

3. Special gowns, shoe, and head covers should be worn before entering 			     the barrier and while working in the ceiling.  Any tool carts or 				     equipment should be left at the exit of the barrier, if possible.

4. Upon leaving the barrier, remove head cover and gown, and then remove 		     one shoe cover at a time, keeping the dirty foot (the one with the shoe 			     cover) in the barrier and placing the clean foot (the one without the shoe 	 	     cover) near the exit of the barrier for Housekeeping to remove.  If carts or 		     equipment must go inside the barrier, they must be covered with a sheet 		     just prior to being removed from the barrier, and must then be taken 			     immediately off the unit.  Absolutely no dust should be carried out of the 		     barrier area.

5. At the completion of the work, Housekeeping should be notified to 			     take down the barrier (assisted by Engineering Services), and perform 			     clean up duties.  Housekeeping will need some prior notification, 			     therefore, approximately 30 minutes before the completion of your 			     project, ask the nursing unit clerk to call Housekeeping.  The 				     housekeeper will put on gowns, shoe covers and head covers before 			     entering the barrier.  They will vacuum the floor inside the barrier,			     put all disposable shoe covers and head covers in trash bags and 			     place gowns near the barrier exit.  They will then remove their own 			     head cover and gown, putting the head cover in a trash bag and the 		     	     gown near the exit of the barrier.  They will also remove shoe covers 			     as previously described, prior to coming out of the barrier.  The trash 			     bag will be disposed of in the dirty utility room.  A clean sheet will be 			     placed outside the barrier and all gowns placed on it.  The sheet will 			     wrap all gowns and be placed in the linen bins.

6. Engineering Services will assist with removing the barrier and taking it 			     off the unit immediately Housekeepers will vacuum the area again 			     immediately.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 25, 2016