| SUBJECT/TITLE: | Shutdown or Scheduled Shutdown of Pomerantz Exhaust Fan #1 |
| --- | --- |
| PURPOSE: | To properly shutdown Pomerantz Exhaust Fan #1 |

A. PROCEDURE:

1. Notify the staff in the Eye Department of the shutdown, and the areas 			affected.

2. Check the affected exhaust fan for the following:

a. Control Failure

1. Check the pneumatic - electric switch.

2. Check the operation of the unit on the Metasys Johnson 					Controls computer system.

b. Electrical Problems

1. Check disconnect for power.

c. Mechanical Failure

1. Check the belts, bearings and motors.

3.	If the Environmental Systems Mechanic is unable to identify the problem, 			contact the lead person, Operations Manager of Engineering and the Director 		of Engineering Services as required.

4.	Notify the staff in the Eye Department as to the status of the exhaust fan and the 	length of time required to effect repairs for their planning purposes.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Reviewed: April 25, 2016