| SUBJECT/TITLE: | Maintenance of Pomerantz Exhaust Fan #1 |
| --- | --- |
| PURPOSE: | To properly access CSS area for repair work. |

A. PROCEDURE:

1.	Notify the staff in the Eye Department that the following pressure controlled 		rooms (11153, 11152, 11123B, 11170N) exhaust is off or will be off.

2.	Check the affected exhaust fan for the following:

a. Control Failure

1. Check the pneumatic control compressor.

2. Check the operation of the unit on the Metasys 						Johnson Controls computer system.

b. Electrical Problems

1. Check disconnect for power.

c. Mechanical Failure

1. Check the belts, bearings and motors.

3.	If the Environmental Systems Mechanic is unable to identify the problem, 			contact the lead person, Operations Manager of Engineering Services and 		the Director of Engineering Services, as required.

4.	Notify the staff in the Eye Department as to the status of the exhaust fan and 		the length of time required to effect repairs for their planning purposes.

Related and Supporting Documentation

•	Utilities Management Program, Engineering Services Policy C-001

•	Safety Reference Cards

•	On Call and Call Back Procedures, Engineering Services Policy A-115

Date effective: July 1, 1995

Date Revised: July 28, 2001

Date Reviewed: April 25, 2016